## Information
Field | Value | Unit | Notes
Equipment ID | ABS_2 |  | Internal registry ID
Equipment Type | Absorption Chiller |  | Single-effect hot water type
Manufacturer | YORK (Wuxi) Air Conditioning and Refrigeration Co., Ltd. |  | From datasheet
Manufacturer Model | YHAU-CL500EXE-B |  | From datasheet
Package Version | v2.0 |  | Equipment Package v2.0
Data Confidence | Medium |  | Datasheet + GA drawing; no part-load performance map
Cooling Capacity | 1231 | kW | Rated cooling capacity
Cooling Capacity | 350 | USRT | Rated cooling capacity
COP | 0.77 | kW/kW | Rated single-effect hot water COP
Capacity Control Range | 100 to approx. 20% |  | From datasheet
Power Source | 3 AC 380 V ±10%, 50 Hz ±1Hz
Power Consumption | 13.5 | kW | Total electric power consumption
Electrical Capacity | 16.9 | kVA
Operating Weight | 24 | ton
Shipping Weight | 19.5 | ton
Overall Length | 7000 | mm | Datasheet reference dimension
Overall Width | 2320 | mm | Datasheet reference dimension
Overall Height | 3330 | mm | Datasheet reference dimension
Tube Extracting Space | 5500 | mm | Datasheet
Application | General Air-Conditioning
Installation Condition | Indoors / Non-Explosion-Proof
Evaporator Tube | Copper Tube, 0.8 mm thickness
Absorber/Condenser Tube | SUS316L Tube, 0.8 mm thickness
Pressure Vessel (GB Code) | Not Applicable
Source Datasheet | Dta sheet_YHAU-CL500EXE-BABS.pdf |  | Uploaded PDF
Source GA Drawing | Reference GA drawing_YHAU-CL500EXE(L)-BABS.pdf |  | Uploaded PDF
Created | 2026-06-30 09:02 |  | Generated by ChatGPT

## Metadata
Field | Value | Notes
registry_id | ABS_2 | Internal software ID
equipment_type | absorption_chiller | Used by Equipment Library
equipment_subtype | single_effect_hot_water
cooling_system_family | ABS + Dry Cooler / ABS + Cooling Tower | Potential systems using this equipment
cooling_unit_capacity_mw | 1.5 | Expected mapping based on current registry discussion
manufacturer | YORK
manufacturer_model | YHAU-CL500EXE-B
rated_capacity_kW | 1231
rated_cop | 0.77
rated_electric_power_kW | 13.5 | Auxiliary/pump electric consumption
solver_readiness | Partial | Can be used as rated-point model; part-load map missing
required_for_pue | Yes | ABS heat input and auxiliary power affect PUE
source_type | datasheet + GA drawing
package_standard | Equipment Package v2.0 | One equipment folder, one Excel

## Performance_Map
Parameter | Value | Unit | Source / Notes
Cooling Capacity | 1231 | kW | Datasheet
Cooling Capacity | 350 | USRT | Datasheet
COP | 0.77 | kW/kW | Datasheet
Driving Hot Water Heat Input | 1598 | kW | Datasheet amount of heat
Cooling Water Heat Rejection | 2829 | kW | Datasheet amount of heat
Electric Power Consumption | 13.5 | kW | Datasheet
Capacity Control Minimum | 20 | % | Approximate
Capacity Control Maximum | 100 | %

## Solver_Curve
load_ratio | cooling_capacity_kW | cop | hot_water_heat_input_kW | electric_power_kW | cooling_water_heat_rejection_kW | chw_flow_m3_h | cw_flow_m3_h | hw_flow_m3_h | note
100% | 1231 | 0.77 | 1598 | 13.5 | 2829 | 109.7 | 506.8 | 189 | Simplified proportional curve; replace with manufacturer part-load data when available
80% | 984.8 | 0.77 | 1278.4 | 10.8 | 2263.2 | 87.76 | 405.44 | 151.2 | Simplified proportional curve; replace with manufacturer part-load data when available
60% | 738.6 | 0.77 | 958.8 | 8.1 | 1697.4 | 65.82 | 304.08 | 113.4 | Simplified proportional curve; replace with manufacturer part-load data when available
40% | 492.4 | 0.77 | 639.2 | 5.4 | 1131.6 | 43.88 | 202.72 | 75.6 | Simplified proportional curve; replace with manufacturer part-load data when available
20% | 246.2 | 0.77 | 319.6 | 2.7 | 565.8 | 21.94 | 101.36 | 37.8 | Simplified proportional curve; replace with manufacturer part-load data when available

## Water_Loops
Loop | Fluid | Heat kW | Inlet Temp C | Outlet Temp C | Flow m3/h | Pipe In DN | Pipe Out DN | Passes | Pressure Drop kPa | Max Working Pressure kPa.G | Fouling Factor m2K/kW | Notes
Chilled Water | 25wt% Propylene glycol |  | 32 | 22 | 109.7 | 125 | 125 | 6 | 126 | 1000 | 0.018 | Cooling output loop
Cooling Water | 25wt% Propylene glycol | 2829 | 46 | 51 | 506.8 | 250 | 250 | 4 | 144 | 1000 | 0.044 | Heat rejection loop
Driving Hot Water | Fresh Water | 1598 | 95.5 | 88 | 189 | 250 | 250 | 6 | 85 | 1000 | 0.018 | Driving heat loop

## GA_Drawing
Field | Value | Unit | Source / Notes
GA Drawing Model | YHAU-CL500EXE(L)-BABS |  | GA drawing filename/title
CHW | Chilled Water |  | Drawing legend
CW | Cooling Water |  | Drawing legend
HW | Hot Water |  | Drawing legend
Overall Length | 7000 | mm | Datasheet
Overall Width | 2320 | mm | Datasheet
Overall Height | 3330 | mm | Datasheet
Max Length excluding cooling water pipe | 6490 | mm | GA drawing
Control Panel Max Width | 2270 | mm | GA drawing
Foundation Bolt Width | 1946 | mm | GA drawing
Base Width | 2046 | mm | GA drawing
Tube Extracting Space | 5500 | mm | Datasheet
Maintenance Space | Required for CHW/CW/HW water box |  | GA drawing note
Control Panel Position | Side mounted |  | GA drawing
Removable Pipe for Water Box Maintenance | Required |  | GA drawing note

## Validation
Check Item | Status | Impact | Notes
Datasheet available | PASS | High | YHAU-CL500EXE-B datasheet uploaded
GA drawing available | PASS | Medium | YHAU-CL500EXE(L)-BABS GA drawing uploaded
Rated capacity | PASS | High | 1231 kW
Rated COP | PASS | High | 0.77
Driving hot water heat input | PASS | High | 1598 kW
Cooling water heat rejection | PASS | High | 2829 kW
Water flow and pressure drop | PASS | High | CHW/CW/HW loops available
Electric power consumption | PASS | Medium | 13.5 kW
Part-load performance curve | MISSING | High | Only capacity control range given; no COP/heat input table by load
Hourly Solver readiness | PARTIAL | High | Use simplified proportional curve until part-load map is available
Data confidence | Medium | Medium | Good rated point data, missing part-load map