## Information
Field | Value | Unit / Notes
Equipment ID | DRYCOOLER_2 | Internal registry ID
Equipment Type | Dry Cooler
Manufacturer | Henry Thermal Engineering Team | From source PDF
Manufacturer Model | HDVD2691-2923EC | From source PDF
Configuration Context | ABS + Dry Cooler / 1.5 MW | User-confirmed context
Package Standard | Equipment Package v2.0 | One equipment folder + one standard Excel
Package Status | Draft - Simplified single-point performance | Fan power missing
Data Confidence | Medium | Design point data available; fan power and multi-ambient curve missing
Source Document | 0624_HDVD2691-2923EC_58_50_44_SUS316L ABS DRY 1.5MW DRYCOOLER 2.pdf | Original Henry / Unilab output
Source Tool | Unilab Coils 9.0 ev - build 260604¦E | From source PDF
Customer Date | 2026/6/24 | From source PDF
Offer / Reference | HC34326003Q / ZA_SG096 | From source PDF
Rated Heat Rejection Capacity | 2923.28 | kW
Design Ambient Air Inlet Temperature | 44 | °C
Design Air Outlet Temperature | 55.3 | °C
Design Fluid Inlet Temperature | 58 | °C
Design Fluid Outlet Temperature | 50 | °C
Fluid | Water | 1 bar A
Volumetric Fluid Flow | 318.8 | m³/h
Mass Fluid Flow | 314392 | kg/h
Fluid Velocity | 0.76 | m/s
Fluid Side Pressure Drop | 26.44 | kPa
Volumetric Air Flow | 818058.2 | m³/h
Mass Air Flow | 901073 | kg/h
Face Velocity on Coil | 2.39 | m/s
Air Side Pressure Drop | 165 | Pa
Exchange Surface | 20896.16 | m²
Global Exchange Coefficient | 34 | W/(m²·K)
DTML | 4.1 | °C
Atmospheric Pressure / Altitude | 1.01 bar A / 0.00 m | From source PDF
Manifolds | In: 4 x 139x5 [5 in]; Out: 4 x 139x5 [5 in] | From source PDF

## Metadata
Field | Value | Notes
registry_id | DRYCOOLER_2 | Stable internal ID used by PUE Solver registry
equipment_type | dry_cooler | Lowercase machine-readable type
equipment_display_name | Dry Cooler 2 | Human-readable label
manufacturer | Henry | Standardized manufacturer name
manufacturer_model | HDVD2691-2923EC | Vendor/model identifier
cooling_system_type | abs_drycooler | Confirmed from user context
cooling_unit_capacity_mw | 1.5 | MW
power_source | grid | Assumed for this package unless updated by configuration
curve_library_path | equipment/DRYCOOLER_2/DRYCOOLER_2.xlsx | Recommended package path
primary_solver_sheet | Solver_Curve | Solver should read simplified data here
raw_performance_sheet | Performance_Map | Original design-point data preserved here
package_version | v2.0 | Equipment Package v2.0 standard
created_by | ChatGPT | Standardization assistant
created_date | 2026-06-30 | Current project date
source_file | 0624_HDVD2691-2923EC_58_50_44_SUS316L ABS DRY 1.5MW DRYCOOLER 2.pdf
source_data_type | Single design point | Multi-ambient performance not available
solver_readiness | Conditional | Ready for simplified calculation; fan power missing

## Performance_Map
source_point_id | ambient_air_inlet_C | air_outlet_C | fluid_inlet_C | fluid_outlet_C | heat_rejection_capacity_kW | volumetric_fluid_flow_m3h | mass_fluid_flow_kgh | fluid_velocity_ms | fluid_side_pressure_drop_kPa | volumetric_air_flow_m3h | mass_air_flow_kgh | face_velocity_ms | air_side_pressure_drop_Pa | exchange_surface_m2 | global_exchange_coefficient_W_m2K | DTML_C | fluid | notes
design_44C | 44 | 55.3 | 58 | 50 | 2923.28 | 318.8 | 314392 | 0.76 | 26.44 | 818058.2 | 901073 | 2.39 | 165 | 20896.16 | 34 | 4.1 | Water | Original single design point from Henry / Unilab output

## Solver_Curve
outdoor_dry_bulb_C | heat_rejection_capacity_kW | fan_power_kW | fluid_inlet_C | fluid_outlet_C | fluid_flow_m3h | air_flow_m3h | air_side_pressure_drop_Pa | fluid_side_pressure_drop_kPa | curve_source | solver_status | notes
44 | 2923.28 |  | 58 | 50 | 318.8 | 818058.2 | 165 | 26.44 | single_point_from_performance_map | conditional | Fan power is missing. Solver may use external fan curve/fixed assumption until vendor data is provided.

## Validation
Check Item | Status | Impact on PUE Solver | Recommendation
Source performance report available | PASS | High | Original Henry / Unilab design-point report is available.
Equipment ID confirmed | PASS | High | User requested DRYCOOLER_2.
Manufacturer model available | PASS | Medium | HDVD2691-2923EC identified from source.
Rated heat rejection capacity available | PASS | High | 2923.28 kW at 44°C ambient and 58/50°C water.
Design ambient condition available | PASS | High | 44°C inlet air temperature.
Fluid temperatures available | PASS | High | 58°C inlet / 50°C outlet water.
Fluid flow available | PASS | Medium | 318.8 m³/h.
Air flow available | PASS | Medium | 818,058.2 m³/h.
Air-side pressure drop available | PASS | Low for PUE | Useful for fan/system checks; not directly used in simplified PUE.
Fluid-side pressure drop available | PASS | Medium | Useful for pump/hydraulic consistency check.
Fan power available | MISSING | High | Request fan motor power or fan power curve from vendor.
Multi-ambient performance curve available | MISSING | High | Request performance table across ambient temperatures, e.g. 25/30/35/40/44°C.
Part-load fan control curve available | MISSING | Medium | Request fan speed/load vs power if available.
Solver readiness | CONDITIONAL | High | Can be used for simplified single-point capacity; fan power must come from separate source/assumption.
Data confidence | MEDIUM | High | Good thermal design point; incomplete electrical fan data.