## Information
Field | Value | Unit / Notes
Equipment ID | ABS_1 | Internal registry ID
Equipment Type | Absorption Chiller | Single-effect hot water type
Manufacturer | YORK (Wuxi) Air Conditioning and Refrigeration Co., Ltd. | From data sheet
Manufacturer Model | YHAU-CL400EXE-B | Data sheet model
Drawing Model Reference | YHAU-CL400EXE(L)-BABS | GA drawing reference
Cooling Capacity | 1020 | kW
Cooling Capacity | 290 | USRT
COP | 0.77 | kW/kW
Capacity Control Range | 100 ~ Approx. 20%
Application | General Air-Conditioning
Installation Condition | Indoors / Non-Explosion-Proof
Power Source | 3 Ph / 3 Wires / AC 380 V ±10% / 50 Hz ±1 Hz
Power Consumption | 10.6 | kW
Electric Capacity | 13.2 | kVA
Operating Weight | 20 | ton
Shipping Weight | 16.2 | ton
Overall Length | 5900 | mm, data sheet
Overall Width | 2320 | mm, data sheet
Overall Height | 3330 | mm, data sheet
Tub Extracting Space | 4400 | mm
GA Max Length | 5390 | mm, max length excluding cooling water pipe
GA Max Width | 2320 | mm
GA Max Height | 3330 | mm
GA Base / Foundation Length | 4200 | mm
GA Base / Foundation Width | 2046 | mm
Data Confidence | Medium | Data sheet + GA drawing available; no part-load performance map
Source Files | Data sheet_YHAU-CL400EXE-B ABS.pdf; Reference GA drawing_YHAU-CL400EXE(L)-BABS.pdf
Package Version | v2.0 | Generated by ChatGPT

## Metadata
Field | Value
Registry ID | ABS_1
Equipment Type | ABS
Equipment Name | Single-Effect Hot Water Absorption Chiller
Cooling System Compatibility | ABS_DRYCOOLER
Recommended Configuration | ABS_DRYCOOLER_1MW/1.5MW_GRID_CDU (to be confirmed)
Solver Input Type | Fixed rated point + thermal loops
Performance Map Available | No
Rated COP Available | Yes
Primary Performance Sheet | Performance_Map
Solver Read Sheet | Solver_Curve
Engineering Geometry Available | Yes, GA drawing
Source Data Status | Partial
Needs Future Update | Part-load performance / hot-water temperature map

## Performance_Map
Loop | Parameter | Inlet Temp (C) | Outlet Temp (C) | Flow Rate (m3/h) | Heat / Capacity (kW) | Pressure Drop (kPa) | Pipe Diameter Inlet | Pipe Diameter Outlet | Passes | Fluid | Fouling Factor (m2K/kW) | Max Working Pressure (kPa.G) | Notes
Chilled Water | Cooling capacity | 32 | 22 | 90.9 | 1020 | 112 | DN100 PN10 | DN100 PN10 | 7 | 25 wt% Propylene glycol | 0.018 | 1000 | Evaporator side; CHW
Cooling Water | Heat rejection | 46 | 51 | 419.9 | 2344 | 90 | DN250 PN10 | DN250 PN10 | 4 | 25 wt% Propylene glycol | 0.044 | 1000 | Absorber / condenser side; CW
Driving Hot Water | Driving heat input | 95.5 | 89.3 | 189 | 1324 | 71 | DN250 PN10 | DN250 PN10 | 6 | Fresh Water | 0.018 | 1000 | Hot water driving loop; HW

## Solver_Curve
load_ratio | cooling_capacity_kW | cop | electric_power_kW | driving_hot_water_heat_kW | cooling_water_heat_rejection_kW | chw_in_C | chw_out_C | cw_in_C | cw_out_C | hw_in_C | hw_out_C | chw_flow_m3h | cw_flow_m3h | hw_flow_m3h | status | notes
1 | 1020 | 0.77 | 10.6 | 1324 | 2344 | 32 | 22 | 46 | 51 | 95.5 | 89.3 | 90.9 | 419.9 | 189 | Rated point | Use rated point only; no part-load curve in source

## Geometry
Category | Parameter | Value | Unit | Source / Notes
Overall | Length | 5900 | mm | Data sheet
Overall | Width | 2320 | mm | Data sheet / GA max width
Overall | Height | 3330 | mm | Data sheet / GA max height
Maintenance | Tub Extracting Space | 4400 | mm | Data sheet
Foundation | Foundation Base Length | 4200 | mm | GA drawing
Foundation | Foundation Base Width | 2046 | mm | GA drawing
Pipe | CHW / Cooling Water / Hot Water | CHW, CW, HW connections shown |  | GA drawing
Panel | Control Panel | Located on side elevation |  | GA drawing
Maintenance | Removable Pipe for Water Box Maintenance | Required |  | GA drawing notes

## Validation
Item | Status | Comment
Data sheet available | OK | YHAU-CL400EXE-B data sheet provided
GA drawing available | OK | YHAU-CL400EXE(L)-BABS reference GA drawing provided
Rated cooling capacity | OK | 1020 kW
Rated COP | OK | 0.77
Chilled water condition | OK | 32 -> 22 C, 90.9 m3/h
Cooling water condition | OK | 46 -> 51 C, 419.9 m3/h
Driving hot water condition | OK | 95.5 -> 89.3 C, 189.0 m3/h
Electric power consumption | OK | 10.6 kW
Part-load performance map | Missing | Only capacity control range is provided; no COP/load/temperature map
Hot-water temperature sensitivity | Missing | Needed for more accurate annual ABS modeling
Cooling-water temperature sensitivity | Missing | Needed for 8760 calculation with dry cooler / cooling tower
Solver readiness | Partial | Suitable for rated-point / simplified model; not yet full annual map