## Information
Field | Value | Unit / Notes
Equipment ID | ACC_2 | Internal registry ID
Equipment Type | ACC / Air-Cooled Chiller
Manufacturer | YORK
Manufacturer Model | YVAM1500
Project Name | YVAM-480-US | from report
Unit Tag | CH-1 | from report
Cooling Unit Mapping | 1.5 MW | Confirmed by user: ACC_2
Package Version | v2.0 | Equipment Package Standard
Data Confidence | High | Factory performance report available
Solver Readiness | Ready with AHRI 4-point part-load map | Requires interpolation for 8760 use
Rated Cooling Capacity | 1300 | kW
Total Input Power | 424.2 | kW
Rated COP | 3.064 | kW/kW
NPLV.IP | 8.929 | kW/kW
Refrigerant | R-1234ze
Number of Compressors | 1
Compressor Type | Variable Speed
Compressor Model | M2C-233FAC
Number of Compressor Circuits | 1
Capacity Control | 10% - 100%
Nominal Voltage | 460/3/60 | 414V - 508V limits
Min. Circuit Ampacity | 696 | A
Max. Fuse / CB Rating | 1000 | A
RLA | 571.5 | A
Control kVA | 5 | kVA
Compressor kW | 388.5 | kW
Fan Type | Container ship high efficiency fans with variable speed EC motor and harmonic filter
Fan Quantity | 20
Total Fan Power | 35.79 | kW
Total Air Flow | 140 | m3/s
A-Weighted Sound Power | 97.5 | dB(A)
Shipping Weight | 10884 | kg
Operating Weight | 11203 | kg
Refrigerant Charge | 340 | kg
Overall Length | 11887 | mm
Overall Width | 2235 | mm
Overall Height | 2503 | mm
Source File | 01 YVAM1500 PG25 1300kW Performance Report Rev A.PDF | Uploaded source
Source Page 1 | Full-load design / unit / electrical data
Source Page 2 | Heat exchanger and part-load performance table
Source Page 3 | Sound power levels and notes

## Metadata
Field | Value | Notes
registry_id | ACC_2 | Internal software ID
equipment_type | acc | air_cooled_chiller
manufacturer | YORK
manufacturer_model | YVAM1500
configuration_hint | ACC_1.5MW_* | Depends on configuration package
cooling_unit_capacity_mw | 1.5 | User-confirmed mapping
curve_format | performance_map
primary_solver_sheet | Solver_Curve
raw_map_sheet | Performance_Map
design_ambient_C | 46.1
design_capacity_kW | 1300
design_power_kW | 424.2
design_COP | 3.064
fluid_type | Propylene Glycol | 25% concentration
package_created | 2026-06-30
source_document | YORK Performance Report

## Performance_Map
percent_load | ambient_C | capacity_kW | power_input_kW | unit_efficiency_COP | job_FLA_A | source_page | data_type
100 | 46.1 | 1300 | 424.2 | 3.064 | 571.5 | 2 | Factory AHRI part-load point
75 | 33.6 | 974.9 | 189.6 | 5.143 | 109.5 | 2 | Factory AHRI part-load point
50 | 21.1 | 649.9 | 65.69 | 9.896 | 93.5 | 2 | Factory AHRI part-load point
25 | 12.8 | 325 | 17.06 | 19.04 | 90.5 | 2 | Factory AHRI part-load point

## Solver_Curve
load_ratio | percent_load | ambient_C | capacity_kW | power_input_kW | COP | calculated_COP_check | job_FLA_A | source_note | solver_use
1 | 100 | 46.1 | 1300 | 424.2 | 3.064 | 3.0646 | 571.5 | PDF page 2: Factory AHRI part-load point | Use for interpolation
0.75 | 75 | 33.6 | 974.9 | 189.6 | 5.143 | 5.1419 | 109.5 | PDF page 2: Factory AHRI part-load point | Use for interpolation
0.5 | 50 | 21.1 | 649.9 | 65.69 | 9.896 | 9.8934 | 93.5 | PDF page 2: Factory AHRI part-load point | Use for interpolation
0.25 | 25 | 12.8 | 325 | 17.06 | 19.04 | 19.0504 | 90.5 | PDF page 2: Factory AHRI part-load point | Use for interpolation

## Heat_Exchanger
Section | Parameter | Value | Unit / Notes
Evaporator | Model | EA2914-481-CS-2
Evaporator | Entering Fluid Temperature | 25 | C
Evaporator | Leaving Fluid Temperature | 17 | C
Evaporator | Flow Rate | 40.66 | L/s
Evaporator | Fouling Factor | 0.0176 | m2 K/kW
Evaporator | Fluid Type / Concentration | Propylene Glycol / 25.0 | %
Evaporator | Passes | 2
Evaporator | Pressure Drop | 53.8 | kPa
Evaporator | Minimum Flow Rate | 24.24 | L/s
Evaporator | Maximum Flow Rate | 66.18 | L/s
Condenser (Air Cooled) | Ambient Air Temperature | 46.1 | C
Condenser (Air Cooled) | Altitude | 1000 | m
Condenser (Air Cooled) | Number of Fans | 20
Condenser (Air Cooled) | Total Air Flow | 140 | m3/s
Condenser (Air Cooled) | Total Fan Power | 35.79 | kW

## Sound_Data
percent_load | ambient_C | 63_Hz | 125_Hz | 250_Hz | 500_Hz | 1000_Hz | 2000_Hz | 4000_Hz | 8000_Hz | LWA_dBA | source_page
100 | 46.1 | 103.5 | 96.5 | 96.5 | 93.5 | 92 | 87.5 | 89.5 | 87.5 | 97.5 | 3
75 | 33.6 | 100.5 | 94 | 94 | 91.5 | 89.5 | 86.5 | 86 | 81 | 95 | 3
50 | 21.1 | 93.5 | 87.5 | 87.5 | 85.5 | 83.5 | 81.5 | 81 | 75.5 | 89.5 | 3
25 | 12.8 | 83.5 | 79.5 | 77 | 78.5 | 74.5 | 77.5 | 76.5 | 88 | 88.5 | 3

## Validation
Check Item | Status | Notes
Source PDF read | PASS | YORK YVAM1500 performance report parsed
Equipment ID confirmed | PASS | ACC_2 confirmed by user
Rated capacity | PASS | 1300 kW
Rated power | PASS | 424.2 kW
Rated COP | PASS | 3.064
Part-load performance points | PASS | 100%, 75%, 50%, 25% captured
Ambient-dependent points | PARTIAL | Only AHRI unloading points available, not a full ambient grid
Fan power | PASS | 35.79 kW full-load total fan power captured
Full fan power curve | MISSING | No fan power values by load / ambient in PDF
Condenser heat rejection map | MISSING | Not provided in this YVAM1500 report
Sound data | PASS | Octave bands and LWA captured
Solver readiness | READY_WITH_LIMITATIONS | Can interpolate between four AHRI part-load points
Recommended additional data | REQUEST | Full air-cooled efficiency map across multiple ambient temperatures