## Information
Field | Value | Unit / Notes
Equipment ID | ACC_3 | Internal registry ID
Equipment Type | ACC / Air-Cooled Chiller | YORK YVAM air-cooled magnetic-bearing chiller
Manufacturer | YORK | From source report
Manufacturer Model | YVAM1650 | From source report
Cooling Unit Mapping | ACC / 2 MW | User-confirmed registry mapping
Package Version | v2.0 | Equipment Package v2.0 standard
Data Confidence | Medium | Good manufacturer report; only one ambient point at 44°C
Rated Cooling Capacity | 1719 | kW
Total Input Power | 411.6 | kW
Rated COP / Cooling Efficiency | 4.177 | kW/kW
NPLV.SI | 12.57 | kW/kW
Refrigerant | R-1234ze | GWP=7
Compressor Type | Variable Speed | 1 compressor / 1 circuit
Capacity Control | 10% - 100% | From source report
Design Ambient Air Temperature | 44 | °C
Entering Fluid Temperature | 32 | °C
Leaving Fluid Temperature | 22 | °C
Fluid Type / Concentration | Propylene Glycol / 25.0 | %
Evaporator Flow Rate | 42.97 | L/s
Evaporator Pressure Drop | 58.3 | kPa
Minimum Flow Rate | 24.24 | L/s
Maximum Flow Rate | 67 | L/s
Number of Fans | 26
Total Air Flow | 183 | m3/s
Total Fan Power | 53.11 | kW
Compressor kW | 358.5 | kW
Nominal Voltage | 415/3/50 | V/ph/Hz
Operating Weight | 12624 | kg
Dimensions L x W x H | 15244 x 2235 x 2503 | mm
Source File | ACC DEMO 22 CHLT 44 AMB ACC 2.PDF | YORK Performance Report

## Metadata
Field | Value
registry_id | ACC_3
equipment_id | ACC_3
equipment_type | acc
manufacturer | YORK
manufacturer_model | YVAM1650
cooling_system_type | ACC
cooling_unit_capacity_mw | 2
power_source_compatibility | Grid / Gas Engine
default_folder | equipment/ACC_3/
default_excel | ACC_3.xlsx
solver_ready | YES - single ambient performance map available
requires_interpolation | YES - load interpolation; ambient extrapolation not recommended
source_type | Manufacturer Performance Report
package_standard | Equipment Package v2.0
last_generated | 2026-06-30

## Performance_Map
ambient_C | load_percent | capacity_kW | power_input_kW | unit_efficiency_COP | EFT_C | LFT_C | flow_rate_L_s | evap_PD_kPa | data_source | Notes
44 | 100 | 1719 | 411.6 | 4.177 | 32 | 22 | 42.97 | 58.3 | YORK part-load performance table | Only 44°C ambient is available in the source report.
44 | 90 | 1547 | 357.5 | 4.329 | 32 | 22 | 38.67 | 47.8 | YORK part-load performance table | Do not extrapolate annual performance outside this ambient without additional manufacturer data.
44 | 80 | 1376 | 310.1 | 4.436 | 32 | 22 | 34.38 | 38.3 | YORK part-load performance table | Solver can interpolate by load at 44°C. Multi-ambient map is recommended for 8760 accuracy.
44 | 70 | 1204 | 269.4 | 4.469 | 32 | 22 | 30.08 | 29.7 | YORK part-load performance table
44 | 60 | 1032 | 234 | 4.408 | 32 | 22 | 25.78 | 21.9 | YORK part-load performance table
44 | 50 | 859.7 | 199.7 | 4.304 | 30.87 | 22 | 24.24 | 19.3 | YORK part-load performance table
44 | 40 | 687.8 | 168.6 | 4.08 | 29.09 | 22 | 24.24 | 19.3 | YORK part-load performance table
44 | 30 | 515.8 | 141.1 | 3.655 | 27.32 | 22 | 24.24 | 19.3 | YORK part-load performance table
44 | 20 | 343.9 | 125.4 | 2.743 | 25.55 | 22 | 24.24 | 19.3 | YORK part-load performance table

## Solver_Curve
ambient_C | load_ratio | capacity_kW | power_input_kW | COP | fan_power_kW | compressor_power_kW | total_air_flow_m3_s | notes
44 | 1 | 1719 | 411.6 | 4.177 |  |  |  | fan/compressor split not provided by load; total input power should be used for PUE
44 | 0.9 | 1547 | 357.5 | 4.329 |  |  |  | fan/compressor split not provided by load; total input power should be used for PUE
44 | 0.8 | 1376 | 310.1 | 4.436 |  |  |  | fan/compressor split not provided by load; total input power should be used for PUE
44 | 0.7 | 1204 | 269.4 | 4.469 |  |  |  | fan/compressor split not provided by load; total input power should be used for PUE
44 | 0.6 | 1032 | 234 | 4.408 |  |  |  | fan/compressor split not provided by load; total input power should be used for PUE
44 | 0.5 | 859.7 | 199.7 | 4.304 |  |  |  | fan/compressor split not provided by load; total input power should be used for PUE
44 | 0.4 | 687.8 | 168.6 | 4.08 |  |  |  | fan/compressor split not provided by load; total input power should be used for PUE
44 | 0.3 | 515.8 | 141.1 | 3.655 |  |  |  | fan/compressor split not provided by load; total input power should be used for PUE
44 | 0.2 | 343.9 | 125.4 | 2.743 |  |  |  | fan/compressor split not provided by load; total input power should be used for PUE

## Condenser
ambient_C | load_percent | heat_rejection_kW | discharge_air_temp_C | total_air_flow_m3_s | active_fans | data_source
44 | 100 | 2109 | 53.83 | 183 | 26 | YORK condenser part-load table
44 | 90 | 1882 | 53.22 | 173 | 26 | YORK condenser part-load table
44 | 80 | 1662 | 52.61 | 164 | 26 | YORK condenser part-load table
44 | 70 | 1452 | 52.17 | 151 | 26 | YORK condenser part-load table
44 | 60 | 1245 | 51.44 | 142 | 26 | YORK condenser part-load table
44 | 50 | 1040 | 50.67 | 133 | 26 | YORK condenser part-load table
44 | 40 | 837.7 | 49.56 | 128 | 26 | YORK condenser part-load table
44 | 30 | 641.3 | 48.61 | 118 | 26 | YORK condenser part-load table
44 | 20 | 464 | 49.33 | 74 | 26 | YORK condenser part-load table

## Validation
Check Item | Status | Comment
Manufacturer / Model | PASS | YORK YVAM1650 identified
Rated Capacity | PASS | 1719 kW available
Rated Power | PASS | 411.6 kW available
Rated COP | PASS | 4.177 available
Part-load COP Map | PARTIAL | Only 44°C ambient; 20–100% loads available
Part-load Power Input | PASS | Available at 20–100% loads
Condenser Heat Rejection | PASS | Available at 20–100% loads
Fan Power | PARTIAL | Design total fan power 53.11 kW available, but no part-load fan power curve
Multi-Ambient Performance | MISSING | Needed for more accurate annual 8760 simulation
Minimum Ambient / Max Ambient Envelope | MISSING | Not provided
PUE Solver Readiness | PASS WITH LIMITATION | Usable as a single-ambient performance map
Data Confidence | MEDIUM | Manufacturer report is detailed but ambient coverage is limited