## Information
Field | Value | Unit/Notes
Equipment ID | CENTRIFUGALCHILLER_1 | Registry / software ID
Equipment Type | Centrifugal Chiller | Water-cooled chiller
Manufacturer | YORK | From performance report
Manufacturer Model | YKGEELP85ERHS | Model No.
Project / Unit Tag | P07 HDC Project / CH-8 | From report
Rated Net Capacity | 2000 | kW
Specified Net Capacity | 2000 | kW
Total Input Power | 467.7 | kW
Full Load COP | 4.276 | kW/kW
Heat Rejection Capacity | 2431 | kW
Compressor Type | Centrifugal | 1 compressor, 1 circuit
Refrigerant | R-515B
Power Supply | 380/3/50 | V/ph/Hz
Evaporator Water Temperature | 25 -> 19 | °C
Condenser Water Temperature | 52 -> 58 | °C
Evaporator Flow Rate | 79.88 | L/s
Condenser Flow Rate | 98.16 | L/s
Evaporator Pressure Drop | 30.5 | kPa
Condenser Pressure Drop | 25.7 | kPa
Data Confidence | High | Manufacturer performance report with full COP map
Package Standard | Equipment Package v2.0 | One equipment folder + one Excel
Source File | 001-YK-2000KW-380V-50HZ@Evap_25_19-cond_52_58C GB request 2MW Chiller.pdf | Original source PDF

## Metadata
Field | Value
registry_id | CENTRIFUGALCHILLER_1
equipment_id | CENTRIFUGALCHILLER_1
equipment_type | centrifugal_chiller
cooling_system | chiller_drycooler
cooling_unit_capacity_mw | 2
power_source | grid
manufacturer | YORK
manufacturer_model | YKGEELP85ERHS
rated_capacity_kW | 2000
rated_power_kW | 467.7
rated_COP_kW_per_kW | 4.276
curve_type | cop_map
map_independent_variables | CEFT_C, load_percent
map_dependent_variable | COP_kW_per_kW
solver_curve_basis | flattened COP map
package_version | v2.0
data_confidence | High
solver_ready | Yes
last_generated | 2026-06-30

## COP_Map
CEFT_C | 100% Load | 90% Load | 80% Load | 70% Load | 60% Load | 50% Load | 40% Load | 30% Load | 20% Load | 15% Load
52 | 4.276 | 4.284 | 4.229 | 4.159 | 4.132 | 4.006 | 3.816 | 3.531 | 3.1 | 2.784
51.67 | 4.327 | 4.336 | 4.28 | 4.21 | 4.184 | 4.056 | 3.862 | 3.607 | 3.135 | 2.815
48.89 | 4.777 | 4.789 | 4.744 | 4.683 | 4.662 | 4.528 | 4.31 | 3.972 | 3.466 | 3.095
46.11 | 5.282 | 5.319 | 5.345 | 5.286 | 5.253 | 5.079 | 4.805 | 4.41 | 3.839 | 3.425
43.33 | 5.834 | 5.937 | 5.987 | 5.993 | 5.845 | 5.761 | 5.468 | 5.006 | 4.319 | 3.832
40.56 | 6.492 | 6.663 | 6.799 | 6.885 | 6.754 | 6.544 | 6.278 | 5.706 | 4.872 | 4.305
37.78 | 7.256 | 7.478 | 7.679 | 7.838 | 7.859 | 7.584 | 7.231 | 6.536 | 5.524 | 4.844
35 | 8.099 | 8.415 | 8.706 | 8.963 | 9.045 | 8.814 | 8.247 | 7.505 | 6.266 | 5.448
32.22 | 9.138 | 9.54 | 9.923 | 10.28 | 10.45 | 10.3 | 9.583 | 8.662 | 7.162 | 6.172
29.44 | 10.36 | 10.86 | 11.4 | 11.9 | 12.18 | 12 | 11.3 | 9.929 | 8.163 | 6.937
26.67 | 11.82 | 12.56 | 13.33 | 13.95 | 14.2 | 13.84 | 12.87 | 11.2 | 8.914 | 7.5
23.89 | 13.64 | 14.68 | 15.66 | 15.83 | 15.84 | 15.31 | 14.13 | 12.19 | 9.401 | 7.924

## Solver_Curve
CEFT_C | load_percent | load_ratio | capacity_kW | COP_kW_per_kW | estimated_input_power_kW | source
52 | 100 | 1 | 2000 | 4.276 | 467.7268 | PDF Part Load COP Map
52 | 90 | 0.9 | 1800 | 4.284 | 420.1681 | PDF Part Load COP Map
52 | 80 | 0.8 | 1600 | 4.229 | 378.34 | PDF Part Load COP Map
52 | 70 | 0.7 | 1400 | 4.159 | 336.6194 | PDF Part Load COP Map
52 | 60 | 0.6 | 1200 | 4.132 | 290.4163 | PDF Part Load COP Map
52 | 50 | 0.5 | 1000 | 4.006 | 249.6256 | PDF Part Load COP Map
52 | 40 | 0.4 | 800 | 3.816 | 209.6436 | PDF Part Load COP Map
52 | 30 | 0.3 | 600 | 3.531 | 169.9235 | PDF Part Load COP Map
52 | 20 | 0.2 | 400 | 3.1 | 129.0323 | PDF Part Load COP Map
52 | 15 | 0.15 | 300 | 2.784 | 107.7586 | PDF Part Load COP Map
51.67 | 100 | 1 | 2000 | 4.327 | 462.214 | PDF Part Load COP Map
51.67 | 90 | 0.9 | 1800 | 4.336 | 415.1292 | PDF Part Load COP Map
51.67 | 80 | 0.8 | 1600 | 4.28 | 373.8318 | PDF Part Load COP Map
51.67 | 70 | 0.7 | 1400 | 4.21 | 332.5416 | PDF Part Load COP Map
51.67 | 60 | 0.6 | 1200 | 4.184 | 286.8069 | PDF Part Load COP Map
51.67 | 50 | 0.5 | 1000 | 4.056 | 246.5483 | PDF Part Load COP Map
51.67 | 40 | 0.4 | 800 | 3.862 | 207.1466 | PDF Part Load COP Map
51.67 | 30 | 0.3 | 600 | 3.607 | 166.3432 | PDF Part Load COP Map
51.67 | 20 | 0.2 | 400 | 3.135 | 127.5917 | PDF Part Load COP Map
51.67 | 15 | 0.15 | 300 | 2.815 | 106.5719 | PDF Part Load COP Map
48.89 | 100 | 1 | 2000 | 4.777 | 418.6728 | PDF Part Load COP Map
48.89 | 90 | 0.9 | 1800 | 4.789 | 375.8613 | PDF Part Load COP Map
48.89 | 80 | 0.8 | 1600 | 4.744 | 337.2681 | PDF Part Load COP Map
48.89 | 70 | 0.7 | 1400 | 4.683 | 298.9537 | PDF Part Load COP Map
48.89 | 60 | 0.6 | 1200 | 4.662 | 257.4003 | PDF Part Load COP Map
48.89 | 50 | 0.5 | 1000 | 4.528 | 220.8481 | PDF Part Load COP Map
48.89 | 40 | 0.4 | 800 | 4.31 | 185.6148 | PDF Part Load COP Map
48.89 | 30 | 0.3 | 600 | 3.972 | 151.0574 | PDF Part Load COP Map
48.89 | 20 | 0.2 | 400 | 3.466 | 115.4068 | PDF Part Load COP Map
48.89 | 15 | 0.15 | 300 | 3.095 | 96.9305 | PDF Part Load COP Map
46.11 | 100 | 1 | 2000 | 5.282 | 378.6445 | PDF Part Load COP Map
46.11 | 90 | 0.9 | 1800 | 5.319 | 338.4095 | PDF Part Load COP Map
46.11 | 80 | 0.8 | 1600 | 5.345 | 299.3452 | PDF Part Load COP Map
46.11 | 70 | 0.7 | 1400 | 5.286 | 264.8505 | PDF Part Load COP Map
46.11 | 60 | 0.6 | 1200 | 5.253 | 228.4409 | PDF Part Load COP Map
46.11 | 50 | 0.5 | 1000 | 5.079 | 196.8892 | PDF Part Load COP Map
46.11 | 40 | 0.4 | 800 | 4.805 | 166.4932 | PDF Part Load COP Map
46.11 | 30 | 0.3 | 600 | 4.41 | 136.0544 | PDF Part Load COP Map
46.11 | 20 | 0.2 | 400 | 3.839 | 104.1938 | PDF Part Load COP Map
46.11 | 15 | 0.15 | 300 | 3.425 | 87.5912 | PDF Part Load COP Map
43.33 | 100 | 1 | 2000 | 5.834 | 342.818 | PDF Part Load COP Map
43.33 | 90 | 0.9 | 1800 | 5.937 | 303.1834 | PDF Part Load COP Map
43.33 | 80 | 0.8 | 1600 | 5.987 | 267.2457 | PDF Part Load COP Map
43.33 | 70 | 0.7 | 1400 | 5.993 | 233.6059 | PDF Part Load COP Map
43.33 | 60 | 0.6 | 1200 | 5.845 | 205.3037 | PDF Part Load COP Map
43.33 | 50 | 0.5 | 1000 | 5.761 | 173.581 | PDF Part Load COP Map
43.33 | 40 | 0.4 | 800 | 5.468 | 146.3058 | PDF Part Load COP Map
43.33 | 30 | 0.3 | 600 | 5.006 | 119.8562 | PDF Part Load COP Map
43.33 | 20 | 0.2 | 400 | 4.319 | 92.614 | PDF Part Load COP Map
43.33 | 15 | 0.15 | 300 | 3.832 | 78.2881 | PDF Part Load COP Map
40.56 | 100 | 1 | 2000 | 6.492 | 308.0715 | PDF Part Load COP Map
40.56 | 90 | 0.9 | 1800 | 6.663 | 270.1486 | PDF Part Load COP Map
40.56 | 80 | 0.8 | 1600 | 6.799 | 235.3287 | PDF Part Load COP Map
40.56 | 70 | 0.7 | 1400 | 6.885 | 203.3406 | PDF Part Load COP Map
40.56 | 60 | 0.6 | 1200 | 6.754 | 177.6725 | PDF Part Load COP Map
40.56 | 50 | 0.5 | 1000 | 6.544 | 152.8117 | PDF Part Load COP Map
40.56 | 40 | 0.4 | 800 | 6.278 | 127.4291 | PDF Part Load COP Map
40.56 | 30 | 0.3 | 600 | 5.706 | 105.1525 | PDF Part Load COP Map
40.56 | 20 | 0.2 | 400 | 4.872 | 82.1018 | PDF Part Load COP Map
40.56 | 15 | 0.15 | 300 | 4.305 | 69.6864 | PDF Part Load COP Map
37.78 | 100 | 1 | 2000 | 7.256 | 275.634 | PDF Part Load COP Map
37.78 | 90 | 0.9 | 1800 | 7.478 | 240.7061 | PDF Part Load COP Map
37.78 | 80 | 0.8 | 1600 | 7.679 | 208.3605 | PDF Part Load COP Map
37.78 | 70 | 0.7 | 1400 | 7.838 | 178.617 | PDF Part Load COP Map
37.78 | 60 | 0.6 | 1200 | 7.859 | 152.6912 | PDF Part Load COP Map
37.78 | 50 | 0.5 | 1000 | 7.584 | 131.8565 | PDF Part Load COP Map
37.78 | 40 | 0.4 | 800 | 7.231 | 110.6348 | PDF Part Load COP Map
37.78 | 30 | 0.3 | 600 | 6.536 | 91.7993 | PDF Part Load COP Map
37.78 | 20 | 0.2 | 400 | 5.524 | 72.4113 | PDF Part Load COP Map
37.78 | 15 | 0.15 | 300 | 4.844 | 61.9323 | PDF Part Load COP Map
35 | 100 | 1 | 2000 | 8.099 | 246.9441 | PDF Part Load COP Map
35 | 90 | 0.9 | 1800 | 8.415 | 213.9037 | PDF Part Load COP Map
35 | 80 | 0.8 | 1600 | 8.706 | 183.7813 | PDF Part Load COP Map
35 | 70 | 0.7 | 1400 | 8.963 | 156.1977 | PDF Part Load COP Map
35 | 60 | 0.6 | 1200 | 9.045 | 132.67 | PDF Part Load COP Map
35 | 50 | 0.5 | 1000 | 8.814 | 113.4559 | PDF Part Load COP Map
35 | 40 | 0.4 | 800 | 8.247 | 97.005 | PDF Part Load COP Map
35 | 30 | 0.3 | 600 | 7.505 | 79.9467 | PDF Part Load COP Map
35 | 20 | 0.2 | 400 | 6.266 | 63.8366 | PDF Part Load COP Map
35 | 15 | 0.15 | 300 | 5.448 | 55.0661 | PDF Part Load COP Map
32.22 | 100 | 1 | 2000 | 9.138 | 218.8663 | PDF Part Load COP Map
32.22 | 90 | 0.9 | 1800 | 9.54 | 188.6792 | PDF Part Load COP Map
32.22 | 80 | 0.8 | 1600 | 9.923 | 161.2416 | PDF Part Load COP Map
32.22 | 70 | 0.7 | 1400 | 10.28 | 136.1868 | PDF Part Load COP Map
32.22 | 60 | 0.6 | 1200 | 10.45 | 114.8325 | PDF Part Load COP Map
32.22 | 50 | 0.5 | 1000 | 10.3 | 97.0874 | PDF Part Load COP Map
32.22 | 40 | 0.4 | 800 | 9.583 | 83.4812 | PDF Part Load COP Map
32.22 | 30 | 0.3 | 600 | 8.662 | 69.2681 | PDF Part Load COP Map
32.22 | 20 | 0.2 | 400 | 7.162 | 55.8503 | PDF Part Load COP Map
32.22 | 15 | 0.15 | 300 | 6.172 | 48.6066 | PDF Part Load COP Map
29.44 | 100 | 1 | 2000 | 10.36 | 193.0502 | PDF Part Load COP Map
29.44 | 90 | 0.9 | 1800 | 10.86 | 165.7459 | PDF Part Load COP Map
29.44 | 80 | 0.8 | 1600 | 11.4 | 140.3509 | PDF Part Load COP Map
29.44 | 70 | 0.7 | 1400 | 11.9 | 117.6471 | PDF Part Load COP Map
29.44 | 60 | 0.6 | 1200 | 12.18 | 98.5222 | PDF Part Load COP Map
29.44 | 50 | 0.5 | 1000 | 12 | 83.3333 | PDF Part Load COP Map
29.44 | 40 | 0.4 | 800 | 11.3 | 70.7965 | PDF Part Load COP Map
29.44 | 30 | 0.3 | 600 | 9.929 | 60.429 | PDF Part Load COP Map
29.44 | 20 | 0.2 | 400 | 8.163 | 49.0016 | PDF Part Load COP Map
29.44 | 15 | 0.15 | 300 | 6.937 | 43.2464 | PDF Part Load COP Map
26.67 | 100 | 1 | 2000 | 11.82 | 169.2047 | PDF Part Load COP Map
26.67 | 90 | 0.9 | 1800 | 12.56 | 143.3121 | PDF Part Load COP Map
26.67 | 80 | 0.8 | 1600 | 13.33 | 120.03 | PDF Part Load COP Map
26.67 | 70 | 0.7 | 1400 | 13.95 | 100.3584 | PDF Part Load COP Map
26.67 | 60 | 0.6 | 1200 | 14.2 | 84.507 | PDF Part Load COP Map
26.67 | 50 | 0.5 | 1000 | 13.84 | 72.2543 | PDF Part Load COP Map
26.67 | 40 | 0.4 | 800 | 12.87 | 62.1601 | PDF Part Load COP Map
26.67 | 30 | 0.3 | 600 | 11.2 | 53.5714 | PDF Part Load COP Map
26.67 | 20 | 0.2 | 400 | 8.914 | 44.8732 | PDF Part Load COP Map
26.67 | 15 | 0.15 | 300 | 7.5 | 40 | PDF Part Load COP Map
23.89 | 100 | 1 | 2000 | 13.64 | 146.6276 | PDF Part Load COP Map
23.89 | 90 | 0.9 | 1800 | 14.68 | 122.6158 | PDF Part Load COP Map
23.89 | 80 | 0.8 | 1600 | 15.66 | 102.1711 | PDF Part Load COP Map
23.89 | 70 | 0.7 | 1400 | 15.83 | 88.4397 | PDF Part Load COP Map
23.89 | 60 | 0.6 | 1200 | 15.84 | 75.7576 | PDF Part Load COP Map
23.89 | 50 | 0.5 | 1000 | 15.31 | 65.3168 | PDF Part Load COP Map
23.89 | 40 | 0.4 | 800 | 14.13 | 56.6171 | PDF Part Load COP Map
23.89 | 30 | 0.3 | 600 | 12.19 | 49.2207 | PDF Part Load COP Map
23.89 | 20 | 0.2 | 400 | 9.401 | 42.5487 | PDF Part Load COP Map
23.89 | 15 | 0.15 | 300 | 7.924 | 37.8597 | PDF Part Load COP Map

## Heat_Exchanger
Section | Parameter | Value | Unit
Evaporator | Fluid Type | Water
Evaporator | Passes | 2
Evaporator | Fouling Factor | 0.0176 | m2 K/kW
Evaporator | Entering Fluid Temperature | 25 | °C
Evaporator | Leaving Fluid Temperature | 19 | °C
Evaporator | Flow Rate | 79.88 | L/s
Evaporator | Pressure Drop | 30.5 | kPa
Evaporator | Minimum Flow Rate | 47.62 | L/s
Evaporator | Maximum Flow Rate | 181.2 | L/s
Condenser | Fluid Type | Water
Condenser | Passes | 2
Condenser | Fouling Factor | 0.044 | m2 K/kW
Condenser | Entering Fluid Temperature | 52 | °C
Condenser | Leaving Fluid Temperature | 58 | °C
Condenser | Flow Rate | 98.16 | L/s
Condenser | Pressure Drop | 25.7 | kPa
Condenser | Minimum Flow Rate | 65.43 | L/s
Condenser | Maximum Flow Rate | 235.8 | L/s

## Validation
Check Item | Status | Notes
Rated capacity available | PASS | 2000 kW
Rated input power available | PASS | 467.7 kW
Rated COP available | PASS | 4.276 kW/kW
CEFT x Load COP map available | PASS | 12 CEFT rows × 10 load columns
Evaporator water data available | PASS | 25/19°C, 79.88 L/s
Condenser water data available | PASS | 52/58°C, 98.16 L/s
Pressure drops available | PASS | Evap 30.5 kPa; Cond 25.7 kPa
Sound table available | PARTIAL | Source PDF has sound pressure table; not required for PUE Solver
IPLV/NPLV available | MISSING | PDF warning says no IPLV/NPLV value
PUE Solver readiness | READY | Use COP_Map or Solver_Curve for interpolation