## SPEC
PROJECT NAME
PROJECT LOCALTION
BRAND
MODEL
COUNTRY OF ORIGIN
|  |  | EQUIPMENT TYPE | EQUIPMENT TYPE | EQUIPMENT TYPE | Dry Cooler
|  |  | Revision | Revision | Revision | N
|  |  | Submital Date | Submital Date | Submital Date | 2026-01-19
Specification | 1 | General Requirement |  |  |  | Response | Remark
| 1.1 | Installation Area | 40-foot container with a height of 3400mm | 40-foot container with a height of 3400mm | 40-foot container with a height of 3400mm
| 1.2 | Ambient Temperature Range, ℃ | 46 | 42 | 38.8
| 1.3 | Voltage (V) | 480V | 480V | 480V
| 1.4 | Frequency (Hz) | 60Hz | 60Hz | 60Hz
| 1.5 | Phases | 3N | 3N | 3N
| 1.6 | Norminal Input Power(kW) | 261.3 | 261.3 | 261.3
| 1.7 | Unit Dimension (WxLxH) (mm) | 2438*12032*3400 | 2438*12032*3400 | 2438*12032*3400
| 1.8 | Equipment Weight (kg) | 16000~17000 | 16000~17000 | 16000~17000
| 1.9 | Shipping Weight (kg) | 16000~17000 | 16000~17000 | 16000~17000
| 1.1 | Operation Weight (kg) | 22000 | 22000 | 22000
| 1.11 | Elevation (m) | 0 | 0 | 0
| 2 | Operation mode |  |  |  | Response | Remark
| 2.1 | Heat Rejection(kW) | 2532 | 3401 | 4107
| 2.2 | Entering Water(℃) | 58 | 58 | 58
| 2.3 | Leaving Water(℃) | 52 | 49.9 | 48.3
| 2.4 | Entering Air Dry Bulb(℃) | 46 | 42 | 38.8
| 2.5 | Water Flow Rate(l/h) | 366974 | 366974 | 366974
| 2.6 | Water pressure drop(kPa) | 94.3 | 94.7 | 949
| 3 | Contruction |  |  |  | Response | Remark
| 3.1 | Tube Material | SS304 | SS304 | SS304
| 3.2 | Fin Material | Al | Al | Al
| 3.3 | Unit Color | Please Inform | Please Inform | Please Inform
| 4 | Fan |  |  |  | Response | Remark
| 4.1 | Air Flow(m3/h) | 820000 | 820000 | 820000
| 4.2 | External Satic Pressure(Pa) | 212 | 212 | 212
| 4.3 | Fan Type | Centrifugal | Centrifugal | Centrifugal
| 4.4 | Fans per Dry Cooler(No.) | 78 | 78 | 78
| 4.5 | Fan Motor Min.(kW) | 3.35 | 3.35 | 3.35
| 4.6 | Motor type | EC | EC | EC
| 5 | Piping Dimension |  |  |  | Response | Remark
| 5.1 | Inlet Pipe | 4 x ASME B16.5 NPS 5 Class 150 RF F304 | 4 x ASME B16.5 NPS 5 Class 150 RF F304 | 4 x ASME B16.5 NPS 5 Class 150 RF F304
| 5.2 | Outlet Pipe | 4 x ASME B16.5 NPS 5 Class 150 RF F304 | 4 x ASME B16.5 NPS 5 Class 150 RF F304 | 4 x ASME B16.5 NPS 5 Class 150 RF F304
| 6 | Configurations |  |  |  | Response | Remark
| 6.1 | Controller | PLC | PLC | PLC
| 6.2 | HMI | Please Inform | Please Inform | Please Inform
| 6.3 | Communication Protocol | MODBUS-TCP | MODBUS-TCP | MODBUS-TCP
| 6.4 | Control Model | Local/BA Control | Local/BA Control | Local/BA Control
| 6.5 | Start-Up/Stop Command | Local/BA Control | Local/BA Control | Local/BA Control
| 6.6 | Wiring | Integrated in Unit | Integrated in Unit | Integrated in Unit
| 7 | Others |  |  |  | Response | Remark
| 7.1 | All piping, valves and wiring shall be factory installed and internal to each unit (i.e. no external field installed components).
| 7.2 | Unit CERTIFICATION | UL & ETL | UL & ETL | UL & ETL
| 7.3 | Label: All Label need EN version, not allow to use CN
| 7.4 | Provide 3D Modeling in stp format
Update Record | Rev | Update Discription |  |  |  |  | Data
| N | Newly released |  |  |  |  | 2026-01-19

## Sheet1
Ambient Temperature Range, ℃ | 46 | 44 | 42 | 38.8
Heat Rejection(kW) | 2532 | 3065 | 3401 | 4107
Entering Water(℃) | 58 | 58 | 58 | 58
Leaving Water(℃) | 52 | 52 | 49.9 | 48.3
Entering Air Dry Bulb(℃) | 46 | 44 | 42 | 38.8
Water Flow Rate(l/h) | 366974 | 444332 | 366974 | 366974
Water pressure drop(kPa) | 94.3 | 110 | 94.7 | 949
[5 empty] | Ambient °C | 定流量 Flow L/h | 定流量 Heat Rejection kW | 定流量 ΔT °C | 定温差 Flow L/h | 定温差 Heat Rejection kW | 定温差 ΔT °C
[5 empty] | 33 | 366974 | 5315 | 12.49 | 896382 | 5654 | 6
[5 empty] | 34 | 366974 | 5102 | 11.99 | 855637 | 5393 | 6
[5 empty] | 35 | 366974 | 4890 | 11.49 | 814893 | 5131 | 6
[5 empty] | 36 | 366974 | 4677 | 10.99 | 774148 | 4869 | 6
[5 empty] | 37 | 366974 | 4465 | 10.49 | 733403 | 4607 | 6
[5 empty] | 38 | 366974 | 4252 | 9.99 | 692659 | 4345 | 6
[5 empty] | 39 | 366974 | 4039 | 9.5 | 651914 | 4081 | 6
[5 empty] | 40 | 366974 | 3827 | 9 | 611170 | 3820 | 6
[5 empty] | 41 | 366974 | 3614 | 8.5 | 570425 | 3558 | 6
[5 empty] | 42 | 366974 | 3402 | 8 | 529680 | 3296 | 6
[5 empty] | 43 | 366974 | 3189 | 7.49 | 488936 | 3034 | 6
[5 empty] | 44 | 366974 | 2976 | 7 | 448191 | 2777 | 6
[5 empty] | 45 | 366974 | 2764 | 6.5 | 407446 | 2515 | 6
[5 empty] | 46 | 366974 | 2551 | 6 | 366702 | 2551 | 6