## Information
Parameter | Value | Unit | Source
Equipment Type | CDU | - | Configuration
Model ID | CDU_2 | - | Configuration
Configuration | ACC_1.5MW_GASENGINE_CDU | - | Configuration
Maximum Power | 22 | kW | Engineering Assumption
Base Power | 5.5 | kW | 25% of maximum power
Control Mode | Base Power + Quadratic Load Curve | - | Engineering Model
Curve Formula | P = 5.5 + (22 - 5.5) × load_ratio² | - | Engineering Model
Load Ratio Range | 0.10 - 1.00 | - | Software Lookup
Primary Read Sheet | Solver_Curve | - | PUE Solver
Notes | CDU total power includes fixed controls/auxiliaries plus variable pump power. | - | Engineering
Data Status | Estimated curve; replace with vendor curve when available. | - | Engineering

## Metadata
Item | Value
Version | v2.0
Status | Engineering Estimated Curve
Author | ChatGPT
Data Source | Engineering assumption based on CDU fixed auxiliary power and variable pump power
Maximum Power | 22 kW
Base Power | 5.5 kW
Curve Type | Quadratic with base power
Formula | P=5.5+(22-5.5)×L²
Validation | Pending vendor performance data

## Performance_Map
load_ratio | base_power_kW | variable_power_kW | total_power_kW | curve_basis | notes
0.1 | 5.5 | 0.17 | 5.67 | P=5.5+(22-5.5)×L² | Minimum modeled load point
0.15 | 5.5 | 0.37 | 5.87 | P=5.5+(22-5.5)×L² | Interpolated engineering point
0.2 | 5.5 | 0.66 | 6.16 | P=5.5+(22-5.5)×L² | Interpolated engineering point
0.25 | 5.5 | 1.03 | 6.53 | P=5.5+(22-5.5)×L² | Interpolated engineering point
0.3 | 5.5 | 1.48 | 6.98 | P=5.5+(22-5.5)×L² | Interpolated engineering point
0.35 | 5.5 | 2.02 | 7.52 | P=5.5+(22-5.5)×L² | Interpolated engineering point
0.4 | 5.5 | 2.64 | 8.14 | P=5.5+(22-5.5)×L² | Interpolated engineering point
0.5 | 5.5 | 4.12 | 9.62 | P=5.5+(22-5.5)×L² | Interpolated engineering point
0.6 | 5.5 | 5.94 | 11.44 | P=5.5+(22-5.5)×L² | Interpolated engineering point
0.7 | 5.5 | 8.08 | 13.58 | P=5.5+(22-5.5)×L² | Interpolated engineering point
0.8 | 5.5 | 10.56 | 16.06 | P=5.5+(22-5.5)×L² | Interpolated engineering point
0.9 | 5.5 | 13.37 | 18.87 | P=5.5+(22-5.5)×L² | Interpolated engineering point
1 | 5.5 | 16.5 | 22 | P=5.5+(22-5.5)×L² | Maximum power point

## Solver_Curve
load_ratio | power_kW
0.1 | 5.67
0.15 | 5.87
0.2 | 6.16
0.25 | 6.53
0.3 | 6.98
0.35 | 7.52
0.4 | 8.14
0.5 | 9.62
0.6 | 11.44
0.7 | 13.58
0.8 | 16.06
0.9 | 18.87
1 | 22

## Validation
Item | Value
Curve Type | Base Power + Quadratic
Maximum Power | 22 kW at load_ratio = 1.00
Base Power | 5.5 kW
Base Power Fraction | 25% of maximum power
Formula | P=5.5+(22-5.5)×L²
Load Ratio Range | 0.10 - 1.00
Monotonic Increase | PASS
Maximum Point Check | PASS: 22.00 kW
Formula Errors | PASS
Validation Status | Engineering estimate
Future Update | Replace with vendor CDU power curve when available