## Information
Parameter | Value | Unit | Source
Equipment Type | RTC | - | Configuration
Model ID | RTC_1.5MW | - | Configuration Naming Standard
Configuration | Cooling Unit 1.5 MW | - | Configuration Library
Control Mode | IT Load Ratio Curve | - | Engineering Fit
Reference IT Load | 1500 | kW | Engineering Assumption
Reference RTC Cooling | 150 | kW | Engineering Assumption
Maximum RTC Fan Power | 12 | kW | Engineering Assumption
Low-Load Flat Anchor Ratio | 0.4 | IT Load Ratio | Leadership Review
Fan Power at 40% Anchor | 3 | kW | Engineering Assumption
Fan Power at 10% Low Load | 2.76 | kW | Engineering Assumption
High-Load Curve Exponent | 2 | - | Engineering Fit
Formula Below 40% | Near-flat interpolation from 2.76 kW @10% to 3.00 kW @40% | - | Engineering Fit
Formula Above 40% | P = 3 + (12 - 3) * ((x - 0.40) / (1 - 0.40))^2 | - | Engineering Fit
Notes | RTC fan power curve scaled from the reviewed 20 kW reference shape to 12 kW maximum for a 1.5 MW cooling unit. | - | Engineering

## Metadata
Item | Value
Version | v1.2
Status | Preliminary Engineering Fit
Author | ChatGPT
Data Source | Engineering curve scaled from reviewed 20 kW RTC reference for 1.5 MW cooling unit
Validation | Pending vendor performance curve / field test data
Model Scope | RTC fan power curve for 1.5 MW cooling unit in PUE Solver
Applicable Range | IT Load Ratio 0.10 to 1.00
Curve Intent | Keep RTC fan power nearly flat below 40% IT load ratio
Caution | Do not treat RTC cooling reduction as linear fan power reduction

## Performance_Map
IT_Load_Ratio | RTC_Cooling_kW | Airflow_Ratio | RTC_Fan_Power_kW | Formula_Basis | Notes
0.1 | 15 | 0.1 | 2.76 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.15 | 22.5 | 0.15 | 2.8 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.2 | 30 | 0.2 | 2.84 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.25 | 37.5 | 0.25 | 2.88 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.3 | 45 | 0.3 | 2.92 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.35 | 52.5 | 0.35 | 2.96 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.4 | 60 | 0.4 | 3 | Scaled low-load near-flat interpolation | Flat anchor at 40%
0.5 | 75 | 0.5 | 3.25 | P=3+(12-3)* ((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.6 | 90 | 0.6 | 4 | P=3+(12-3)* ((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.7 | 105 | 0.7 | 5.25 | P=3+(12-3)* ((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.8 | 120 | 0.8 | 7 | P=3+(12-3)* ((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.9 | 135 | 0.9 | 9.25 | P=3+(12-3)* ((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
1 | 150 | 1 | 12 | P=3+(12-3)* ((x-0.40)/(1-0.40))^2 | Maximum power at 100% reference load

## Solver_Curve
load_ratio | power_kW
0.1 | 2.76
0.15 | 2.8
0.2 | 2.84
0.25 | 2.88
0.3 | 2.92
0.35 | 2.96
0.4 | 3
0.5 | 3.25
0.6 | 4
0.7 | 5.25
0.8 | 7
0.9 | 9.25
1 | 12

## Validation
Item | Value
Curve Type | Near-flat low-load RTC fan curve
Validation Status | Preliminary
Maximum Power | 12 kW at 100% IT Load Ratio
Flat Region Intent | Below 40% IT Load Ratio, fan power changes only slightly
40% Anchor | 3.00 kW
10% Low-Load Estimate | 2.76 kW
High-Load Formula | P = 3 + (12 - 3) * ((x - 0.40) / 0.60)^2
Missing Data | Vendor RTC fan curve / field commissioning data
Future Update | Replace engineering fit with vendor curve when available
Software Read Sheet | Solver_Curve
Software Read Columns | load_ratio, power_kW