## Information
Parameter | Value | Unit | Source
Equipment Type | Electrical Distribution | - | Configuration
Model ID | ELECTRICAL_DISTRIBUTION_1 | - | Configuration
Configuration | Standard Package | - | Configuration
IT Path Efficiency | 0.9723 | fraction | Leadership definition
MEP Path Efficiency | 0.9959 | fraction | Leadership definition
Notes | Electrical path package for PUE Solver | - | Engineering

## Metadata
Item | Value
Version | v1.0
Status | Preliminary
Author | ChatGPT
Data Source | Leadership electrical path table
Validation | Approved for Phase 1

## IT_Path
Component | Efficiency | Notes
Main Switchgear | 0.9999 | IT distribution path
UPS | 0.973 | IT path only
Busway / PDU | 0.9995 | Rack distribution
Final Cable / Terminal | 0.9999 | Final feeders
Overall IT Path Efficiency | 0.9723 | Used to convert IT terminal load

## MEP_Path
Component | Efficiency | Notes
MEP Switchgear | 0.9999 | MEP path
MEP MCC / VFD / Feeder | 0.998 | Pumps, fans, auxiliaries
MEP Cable / Bus | 0.998 | Final MEP distribution
Overall MEP Path Efficiency | 0.9959 | Used to convert MEP terminal load

## Solver
Path | overall_efficiency
IT | 0.9723
MEP | 0.9959

## Validation
Item | Value
Calculation Convention | Loss = Load/path efficiency - Load
IT Path | Use overall IT efficiency
MEP Path | Use overall MEP efficiency
Future Update | Support efficiency curves for UPS/VFD if available