## Information
Parameter | Value | Unit | Source
Equipment Type | Engine Radiator | - | Configuration
Equipment ID | ENGINE_RADIATOR_1 | - | Configuration Library
Control Strategy | Single Solver Curve | - | Engineering Model
Rated Maximum Power | 24 | kW | Engineering Assumption
Base Power | 6 | kW | 25% of maximum power
Load Ratio Basis | Engine Output / Rated Engine Output | - | Same philosophy as CW Pump
Curve Type | Base Power + Cubic Affinity Curve | - | Axial Fan Approximation
Formula | P = Pbase + (Pmax-Pbase) × Load Ratio³ | - | Engineering Model

## Metadata
Item | Value
Version | v1.0
Equipment | ENGINE_RADIATOR_1
Maximum Fan Power | 24 kW
Curve Model | Cubic fan affinity with base power
Load Ratio | Engine output ratio

## Performance_Map
load_ratio | base_power_kW | variable_power_kW | total_power_kW | curve_basis
0.1 | 6 | 0.02 | 6.02 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.15 | 6 | 0.06 | 6.06 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.2 | 6 | 0.14 | 6.14 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.25 | 6 | 0.28 | 6.28 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.3 | 6 | 0.49 | 6.49 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.35 | 6 | 0.77 | 6.77 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.4 | 6 | 1.15 | 7.15 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.5 | 6 | 2.25 | 8.25 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.6 | 6 | 3.89 | 9.89 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.7 | 6 | 6.17 | 12.17 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.8 | 6 | 9.22 | 15.22 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.9 | 6 | 13.12 | 19.12 | P=Pbase+(Pmax-Pbase)*load_ratio^3
1 | 6 | 18 | 24 | P=Pbase+(Pmax-Pbase)*load_ratio^3

## Solver_Curve
load_ratio | power_kW
0.1 | 6.02
0.15 | 6.06
0.2 | 6.14
0.25 | 6.28
0.3 | 6.49
0.35 | 6.77
0.4 | 7.15
0.5 | 8.25
0.6 | 9.89
0.7 | 12.17
0.8 | 15.22
0.9 | 19.12
1 | 24

## Validation
Item | Value
Curve Structure | Single Solver_Curve
Normal / Failure | Same curve
Maximum Power Check | 24 kW @ load_ratio=1.0
Formula | P=6+(24-6)*load_ratio^3