## Information
Parameter | Value | Unit | Source
Equipment Type | ACC | - | PUE Solver Configuration Library
Equipment ID | ACC_1 | - | User naming
Manufacturer | YORK | - | Performance Report
Model | YVAM1500 | - | Performance Report
Cooling Mode | Air Cooled Efficiency Map w/VPF | - | Performance Report / Annual kWh workbook
Refrigerant | R-1234ze | - | Performance Report
Number of Compressors | 1 | - | Performance Report
Compressor Type | Variable Speed | - | Performance Report
Capacity Control | 10% - 100% | - | Performance Report
Design Cooling Capacity | 1300 | kW | Performance Report Page 1
Design Ambient | 46.1 | °C | Performance Report Page 2
Design Entering / Leaving Fluid | 25 / 17 | °C | Performance Report Page 2
Design Total Input Power | 424.2 | kW | Performance Report Page 1
Design COP | 3.064 | kW/kW | Performance Report Page 1
Design Total Fan Power | 35.79 | kW | Performance Report Page 2
Source Temperature Range | -5°C to 46.1°C | Ambient Dry Bulb | Annual kWh workbook + PDF design point
Source Load Range | 15% to 100% | Percent Load | Annual kWh workbook
Software Read Sheet | Solver_Curve | - | PUE Solver Standard
Primary Interpolation Inputs | ambient_C, load_ratio | - | PUE Solver Standard
Primary Outputs | capacity_kW, power_input_kW, unit_efficiency_kW_per_kW | - | PUE Solver Standard

## Metadata
Item | Value
Version | v1.0
Status | Vendor PDF + Annual Estimate Data Combined
Author | ChatGPT
Created For | ACC_1/ YVAM1500 performance library
Source 1 | 01 YVAM1500 PG25 1300kW Performance Report Rev A.PDF
Source 1 Range | Design point 1300 kW at 46.1°C; 25/17°C fluid; 424.2 kW total input
Source 2 | 003-Estimate Annual kWh_YVAM1500 @W17& W25-1300kW-2025_5_8.xlsx
Source 2 Range | Ambient -5°C to 45°C; loads 15% to 100%; W25/W17 reference matrix
Priority Rule | PDF design point overrides annual workbook at 100% load / 46.1°C
Important Note | The annual workbook contains estimated performance values; only the PDF design point is explicitly certified in the supplied PDF.
Validation | Ready for software testing; vendor confirmation recommended before production use

## Efficiency_Map
Ambient_C | Load_100% | Load_90% | Load_80% | Load_70% | Load_60% | Load_50% | Load_40% | Load_30% | Load_20% | Load_15%
-5 | 22.27 | 24.72 | 29.46 | 33.18 | 34.62 | 35.29 | 31.57 | 24.63 | 18.67 | 15.27
-3 | 21.94 | 24.29 | 28.99 | 32.81 | 34.68 | 35.59 | 31.35 | 24.47 | 18.83 | 15.25
0 | 20.82 | 23.11 | 27.56 | 31.46 | 34.62 | 35.1 | 30.96 | 24.42 | 18.21 | 14.61
3 | 19.56 | 21.32 | 24.94 | 28.34 | 30.74 | 31.77 | 29.46 | 23.88 | 18.76 | 15.07
6 | 17.76 | 19.22 | 21.52 | 24.77 | 27.26 | 29.07 | 28.78 | 23.99 | 18.49 | 15.09
9 | 15.51 | 16.47 | 18.2 | 20.6 | 22.53 | 24.37 | 26.4 | 23.18 | 18.15 | 14.93
11 | 14.05 | 14.73 | 16.07 | 17.64 | 19.63 | 21.56 | 23.38 | 22.23 | 17.57 | 14.77
14 | 12.09 | 12.39 | 13.33 | 14.34 | 15.38 | 16.48 | 17.5 | 18.05 | 16.5 | 13.87
17 | 10.41 | 10.59 | 11.22 | 11.91 | 12.58 | 13.14 | 13.49 | 13.32 | 12.33 | 11.09
20 | 9.041 | 9.154 | 9.607 | 10.07 | 10.49 | 10.81 | 10.85 | 10.55 | 9.371 | 8.16
23 | 7.923 | 7.977 | 8.301 | 8.618 | 8.884 | 9.027 | 8.956 | 8.505 | 7.283 | 6.247
25 | 7.295 | 7.323 | 7.576 | 7.809 | 7.993 | 8.044 | 7.961 | 7.509 | 6.338 | 5.245
28 | 6.441 | 6.45 | 6.63 | 6.775 | 6.86 | 6.819 | 6.586 | 6.044 | 4.887 | 3.748
31 | 5.745 | 5.708 | 5.821 | 5.883 | 5.915 | 5.832 | 5.562 | 5.012 | 3.873 | 2.938
34 | 5.118 | 5.056 | 5.13 | 5.184 | 5.153 | 5.026 | 4.738 | 4.252 | 3.221 | 2.401
36 | 4.759 | 4.682 | 4.712 | 4.724 | 4.686 | 4.56 | 4.291 | 3.855 | 2.771 | 2.15
39 | 4.257 | 4.172 | 4.212 | 4.199 | 4.105 | 3.948 | 3.651 | 3.166 | 2.372 | 1.876
42 | 3.812 | 3.729 | 3.747 | 3.721 | 3.647 | 3.5 | 3.221 | 2.741 | 2.115 | 1.632
45 | 3.418 | 3.34 | 3.334 | 3.315 | 3.247 | 3.112 | 2.864 | 2.459 | 1.87 | 1.334
46.1 | 3.064

## Power_Input_Map
Ambient_C | Load_100% | Load_90% | Load_80% | Load_70% | Load_60% | Load_50% | Load_40% | Load_30% | Load_20% | Load_15%
-5 | 58.36 | 47.34 | 35.32 | 27.42 | 22.53 | 18.42 | 16.48 | 15.83 | 13.93 | 12.77
-3 | 59.26 | 48.18 | 35.88 | 27.75 | 22.48 | 18.27 | 16.58 | 15.94 | 13.81 | 12.78
0 | 62.43 | 50.62 | 37.73 | 28.92 | 22.52 | 18.53 | 16.79 | 15.96 | 14.28 | 13.34
3 | 66.47 | 54.89 | 41.71 | 32.1 | 25.37 | 20.45 | 17.65 | 16.33 | 13.86 | 12.94
6 | 73.2 | 60.87 | 48.31 | 36.73 | 28.62 | 22.36 | 18.07 | 16.26 | 14.06 | 12.92
9 | 83.85 | 71.03 | 57.14 | 44.17 | 34.62 | 26.67 | 19.69 | 16.82 | 14.32 | 13.06
11 | 92.56 | 79.45 | 64.74 | 51.59 | 39.76 | 30.14 | 22.24 | 17.55 | 14.8 | 13.2
14 | 107.5 | 94.44 | 78.02 | 63.48 | 50.72 | 39.44 | 29.72 | 21.61 | 15.76 | 14.06
17 | 124.9 | 110.5 | 92.69 | 76.4 | 62.02 | 49.46 | 38.54 | 29.28 | 21.09 | 17.58
20 | 143.8 | 127.8 | 108.3 | 90.35 | 74.36 | 60.12 | 47.93 | 36.98 | 27.75 | 23.9
23 | 164.1 | 146.7 | 125.3 | 105.6 | 87.8 | 72.01 | 58.07 | 45.86 | 35.7 | 31.22
25 | 178.2 | 159.8 | 137.3 | 116.5 | 97.59 | 80.81 | 65.32 | 51.95 | 41.02 | 37.18
28 | 201.8 | 181.4 | 156.9 | 134.3 | 113.7 | 95.33 | 78.95 | 64.53 | 53.21 | 52.03
31 | 226.3 | 205 | 178.7 | 154.7 | 131.9 | 111.5 | 93.49 | 77.81 | 67.13 | 66.35
34 | 254 | 231.4 | 202.7 | 175.5 | 151.4 | 129.3 | 109.8 | 91.72 | 80.73 | 81.25
36 | 273.2 | 249.9 | 220.7 | 192.6 | 166.5 | 142.6 | 121.2 | 101.2 | 93.83 | 90.71
39 | 305.4 | 280.4 | 246.9 | 216.7 | 190 | 164.7 | 142.4 | 123.2 | 109.6 | 103.9
42 | 341.1 | 313.7 | 277.6 | 244.5 | 213.9 | 185.7 | 161.4 | 142.3 | 123 | 119.5
45 | 380.4 | 350.3 | 312 | 274.6 | 240.2 | 208.9 | 181.6 | 158.6 | 139 | 146.2
46.1 | 424.2

## Capacity_Map
Ambient_C | Load_100% | Load_90% | Load_80% | Load_70% | Load_60% | Load_50% | Load_40% | Load_30% | Load_20% | Load_15%
-5 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
-3 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
0 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
3 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
6 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
9 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
11 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
14 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
17 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
20 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
23 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
25 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
28 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
31 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
34 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
36 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
39 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
42 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
45 | 1300 | 1170 | 1040 | 910.2 | 780 | 649.9 | 520.1 | 390 | 260 | 195
46.1 | 1300

## Performance_Map
percent_load | load_ratio | ambient_C | capacity_kW | power_input_kW | unit_efficiency_kW_per_kW | EFT_C | LFT_C | flow_rate_L_s | evap_PD_kPa | source_document | source_page | source_range
100 | 1 | 46.1 | 1300 | 424.2 | 3.064 | 25 | 17 | 40.66 | 53.8 | 01 YVAM1500 PG25 1300kW Performance Report Rev A.PDF | Page 1-2 | PDF design point
100 | 1 | 45 | 1300 | 380.4 | 3.418 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 42 | 1300 | 341.1 | 3.812 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 39 | 1300 | 305.4 | 4.257 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 36 | 1300 | 273.2 | 4.759 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 34 | 1300 | 254 | 5.118 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 31 | 1300 | 226.3 | 5.745 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 28 | 1300 | 201.8 | 6.441 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 25 | 1300 | 178.2 | 7.295 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 23 | 1300 | 164.1 | 7.923 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 20 | 1300 | 143.8 | 9.041 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 17 | 1300 | 124.9 | 10.41 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 14 | 1300 | 107.5 | 12.09 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 11 | 1300 | 92.56 | 14.05 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 9 | 1300 | 83.85 | 15.51 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 6 | 1300 | 73.2 | 17.76 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 3 | 1300 | 66.47 | 19.56 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | 0 | 1300 | 62.43 | 20.82 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | -3 | 1300 | 59.26 | 21.94 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
100 | 1 | -5 | 1300 | 58.36 | 22.27 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 45 | 1170 | 350.3 | 3.34 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 42 | 1170 | 313.7 | 3.729 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 39 | 1170 | 280.4 | 4.172 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 36 | 1170 | 249.9 | 4.682 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 34 | 1170 | 231.4 | 5.056 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 31 | 1170 | 205 | 5.708 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 28 | 1170 | 181.4 | 6.45 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 25 | 1170 | 159.8 | 7.323 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 23 | 1170 | 146.7 | 7.977 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 20 | 1170 | 127.8 | 9.154 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 17 | 1170 | 110.5 | 10.59 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 14 | 1170 | 94.44 | 12.39 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 11 | 1170 | 79.45 | 14.73 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 9 | 1170 | 71.03 | 16.47 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 6 | 1170 | 60.87 | 19.22 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 3 | 1170 | 54.89 | 21.32 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | 0 | 1170 | 50.62 | 23.11 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | -3 | 1170 | 48.18 | 24.29 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
90 | 0.9 | -5 | 1170 | 47.34 | 24.72 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 45 | 1040 | 312 | 3.334 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 42 | 1040 | 277.6 | 3.747 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 39 | 1040 | 246.9 | 4.212 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 36 | 1040 | 220.7 | 4.712 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 34 | 1040 | 202.7 | 5.13 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 31 | 1040 | 178.7 | 5.821 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 28 | 1040 | 156.9 | 6.63 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 25 | 1040 | 137.3 | 7.576 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 23 | 1040 | 125.3 | 8.301 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 20 | 1040 | 108.3 | 9.607 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 17 | 1040 | 92.69 | 11.22 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 14 | 1040 | 78.02 | 13.33 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 11 | 1040 | 64.74 | 16.07 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 9 | 1040 | 57.14 | 18.2 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 6 | 1040 | 48.31 | 21.52 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 3 | 1040 | 41.71 | 24.94 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | 0 | 1040 | 37.73 | 27.56 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | -3 | 1040 | 35.88 | 28.99 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
80 | 0.8 | -5 | 1040 | 35.32 | 29.46 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 45 | 910.2 | 274.6 | 3.315 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 42 | 910.2 | 244.5 | 3.721 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 39 | 910.2 | 216.7 | 4.199 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 36 | 910.2 | 192.6 | 4.724 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 34 | 910.2 | 175.5 | 5.184 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 31 | 910.2 | 154.7 | 5.883 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 28 | 910.2 | 134.3 | 6.775 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 25 | 910.2 | 116.5 | 7.809 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 23 | 910.2 | 105.6 | 8.618 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 20 | 910.2 | 90.35 | 10.07 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 17 | 910.2 | 76.4 | 11.91 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 14 | 910.2 | 63.48 | 14.34 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 11 | 910.2 | 51.59 | 17.64 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 9 | 910.2 | 44.17 | 20.6 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 6 | 910.2 | 36.73 | 24.77 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 3 | 910.2 | 32.1 | 28.34 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | 0 | 910.2 | 28.92 | 31.46 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | -3 | 910.2 | 27.75 | 32.81 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
70 | 0.7 | -5 | 910.2 | 27.42 | 33.18 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 45 | 780 | 240.2 | 3.247 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 42 | 780 | 213.9 | 3.647 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 39 | 780 | 190 | 4.105 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 36 | 780 | 166.5 | 4.686 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 34 | 780 | 151.4 | 5.153 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 31 | 780 | 131.9 | 5.915 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 28 | 780 | 113.7 | 6.86 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 25 | 780 | 97.59 | 7.993 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 23 | 780 | 87.8 | 8.884 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 20 | 780 | 74.36 | 10.49 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 17 | 780 | 62.02 | 12.58 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 14 | 780 | 50.72 | 15.38 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 11 | 780 | 39.76 | 19.63 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 9 | 780 | 34.62 | 22.53 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 6 | 780 | 28.62 | 27.26 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 3 | 780 | 25.37 | 30.74 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | 0 | 780 | 22.52 | 34.62 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | -3 | 780 | 22.48 | 34.68 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
60 | 0.6 | -5 | 780 | 22.53 | 34.62 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 45 | 649.9 | 208.9 | 3.112 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 42 | 649.9 | 185.7 | 3.5 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 39 | 649.9 | 164.7 | 3.948 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 36 | 649.9 | 142.6 | 4.56 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 34 | 649.9 | 129.3 | 5.026 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 31 | 649.9 | 111.5 | 5.832 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 28 | 649.9 | 95.33 | 6.819 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 25 | 649.9 | 80.81 | 8.044 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 23 | 649.9 | 72.01 | 9.027 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 20 | 649.9 | 60.12 | 10.81 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 17 | 649.9 | 49.46 | 13.14 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 14 | 649.9 | 39.44 | 16.48 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 11 | 649.9 | 30.14 | 21.56 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 9 | 649.9 | 26.67 | 24.37 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 6 | 649.9 | 22.36 | 29.07 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 3 | 649.9 | 20.45 | 31.77 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | 0 | 649.9 | 18.53 | 35.1 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | -3 | 649.9 | 18.27 | 35.59 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
50 | 0.5 | -5 | 649.9 | 18.42 | 35.29 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 45 | 520.1 | 181.6 | 2.864 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 42 | 520.1 | 161.4 | 3.221 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 39 | 520.1 | 142.4 | 3.651 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 36 | 520.1 | 121.2 | 4.291 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 34 | 520.1 | 109.8 | 4.738 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 31 | 520.1 | 93.49 | 5.562 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 28 | 520.1 | 78.95 | 6.586 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 25 | 520.1 | 65.32 | 7.961 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 23 | 520.1 | 58.07 | 8.956 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 20 | 520.1 | 47.93 | 10.85 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 17 | 520.1 | 38.54 | 13.49 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 14 | 520.1 | 29.72 | 17.5 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 11 | 520.1 | 22.24 | 23.38 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 9 | 520.1 | 19.69 | 26.4 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 6 | 520.1 | 18.07 | 28.78 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 3 | 520.1 | 17.65 | 29.46 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | 0 | 520.1 | 16.79 | 30.96 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | -3 | 520.1 | 16.58 | 31.35 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
40 | 0.4 | -5 | 520.1 | 16.48 | 31.57 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 45 | 390 | 158.6 | 2.459 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 42 | 390 | 142.3 | 2.741 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 39 | 390 | 123.2 | 3.166 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 36 | 390 | 101.2 | 3.855 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 34 | 390 | 91.72 | 4.252 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 31 | 390 | 77.81 | 5.012 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 28 | 390 | 64.53 | 6.044 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 25 | 390 | 51.95 | 7.509 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 23 | 390 | 45.86 | 8.505 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 20 | 390 | 36.98 | 10.55 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 17 | 390 | 29.28 | 13.32 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 14 | 390 | 21.61 | 18.05 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 11 | 390 | 17.55 | 22.23 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 9 | 390 | 16.82 | 23.18 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 6 | 390 | 16.26 | 23.99 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 3 | 390 | 16.33 | 23.88 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | 0 | 390 | 15.96 | 24.42 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | -3 | 390 | 15.94 | 24.47 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
30 | 0.3 | -5 | 390 | 15.83 | 24.63 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 45 | 260 | 139 | 1.87 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 42 | 260 | 123 | 2.115 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 39 | 260 | 109.6 | 2.372 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 36 | 260 | 93.83 | 2.771 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 34 | 260 | 80.73 | 3.221 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 31 | 260 | 67.13 | 3.873 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 28 | 260 | 53.21 | 4.887 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 25 | 260 | 41.02 | 6.338 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 23 | 260 | 35.7 | 7.283 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 20 | 260 | 27.75 | 9.371 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 17 | 260 | 21.09 | 12.33 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 14 | 260 | 15.76 | 16.5 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 11 | 260 | 14.8 | 17.57 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 9 | 260 | 14.32 | 18.15 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 6 | 260 | 14.06 | 18.49 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 3 | 260 | 13.86 | 18.76 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | 0 | 260 | 14.28 | 18.21 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | -3 | 260 | 13.81 | 18.83 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
20 | 0.2 | -5 | 260 | 13.93 | 18.67 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 45 | 195 | 146.2 | 1.334 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 42 | 195 | 119.5 | 1.632 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 39 | 195 | 103.9 | 1.876 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 36 | 195 | 90.71 | 2.15 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 34 | 195 | 81.25 | 2.401 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 31 | 195 | 66.35 | 2.938 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 28 | 195 | 52.03 | 3.748 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 25 | 195 | 37.18 | 5.245 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 23 | 195 | 31.22 | 6.247 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 20 | 195 | 23.9 | 8.16 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 17 | 195 | 17.58 | 11.09 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 14 | 195 | 14.06 | 13.87 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 11 | 195 | 13.2 | 14.77 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 9 | 195 | 13.06 | 14.93 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 6 | 195 | 12.92 | 15.09 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 3 | 195 | 12.94 | 15.07 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | 0 | 195 | 13.34 | 14.61 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | -3 | 195 | 12.78 | 15.25 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix
15 | 0.15 | -5 | 195 | 12.77 | 15.27 | 25 | 17 |  |  | 003 Annual kWh workbook - YVAM chiller load reference | YVAM chiller load reference | W25/W17 annual estimate matrix

## Solver_Curve
ambient_C | load_ratio | capacity_kW | power_input_kW | unit_efficiency_kW_per_kW | source_range
-5 | 1 | 1300 | 58.36 | 22.27 | annual_estimate_W25_W17
-5 | 0.9 | 1170 | 47.34 | 24.72 | annual_estimate_W25_W17
-5 | 0.8 | 1040 | 35.32 | 29.46 | annual_estimate_W25_W17
-5 | 0.7 | 910.2 | 27.42 | 33.18 | annual_estimate_W25_W17
-5 | 0.6 | 780 | 22.53 | 34.62 | annual_estimate_W25_W17
-5 | 0.5 | 649.9 | 18.42 | 35.29 | annual_estimate_W25_W17
-5 | 0.4 | 520.1 | 16.48 | 31.57 | annual_estimate_W25_W17
-5 | 0.3 | 390 | 15.83 | 24.63 | annual_estimate_W25_W17
-5 | 0.2 | 260 | 13.93 | 18.67 | annual_estimate_W25_W17
-5 | 0.15 | 195 | 12.77 | 15.27 | annual_estimate_W25_W17
-3 | 1 | 1300 | 59.26 | 21.94 | annual_estimate_W25_W17
-3 | 0.9 | 1170 | 48.18 | 24.29 | annual_estimate_W25_W17
-3 | 0.8 | 1040 | 35.88 | 28.99 | annual_estimate_W25_W17
-3 | 0.7 | 910.2 | 27.75 | 32.81 | annual_estimate_W25_W17
-3 | 0.6 | 780 | 22.48 | 34.68 | annual_estimate_W25_W17
-3 | 0.5 | 649.9 | 18.27 | 35.59 | annual_estimate_W25_W17
-3 | 0.4 | 520.1 | 16.58 | 31.35 | annual_estimate_W25_W17
-3 | 0.3 | 390 | 15.94 | 24.47 | annual_estimate_W25_W17
-3 | 0.2 | 260 | 13.81 | 18.83 | annual_estimate_W25_W17
-3 | 0.15 | 195 | 12.78 | 15.25 | annual_estimate_W25_W17
0 | 1 | 1300 | 62.43 | 20.82 | annual_estimate_W25_W17
0 | 0.9 | 1170 | 50.62 | 23.11 | annual_estimate_W25_W17
0 | 0.8 | 1040 | 37.73 | 27.56 | annual_estimate_W25_W17
0 | 0.7 | 910.2 | 28.92 | 31.46 | annual_estimate_W25_W17
0 | 0.6 | 780 | 22.52 | 34.62 | annual_estimate_W25_W17
0 | 0.5 | 649.9 | 18.53 | 35.1 | annual_estimate_W25_W17
0 | 0.4 | 520.1 | 16.79 | 30.96 | annual_estimate_W25_W17
0 | 0.3 | 390 | 15.96 | 24.42 | annual_estimate_W25_W17
0 | 0.2 | 260 | 14.28 | 18.21 | annual_estimate_W25_W17
0 | 0.15 | 195 | 13.34 | 14.61 | annual_estimate_W25_W17
3 | 1 | 1300 | 66.47 | 19.56 | annual_estimate_W25_W17
3 | 0.9 | 1170 | 54.89 | 21.32 | annual_estimate_W25_W17
3 | 0.8 | 1040 | 41.71 | 24.94 | annual_estimate_W25_W17
3 | 0.7 | 910.2 | 32.1 | 28.34 | annual_estimate_W25_W17
3 | 0.6 | 780 | 25.37 | 30.74 | annual_estimate_W25_W17
3 | 0.5 | 649.9 | 20.45 | 31.77 | annual_estimate_W25_W17
3 | 0.4 | 520.1 | 17.65 | 29.46 | annual_estimate_W25_W17
3 | 0.3 | 390 | 16.33 | 23.88 | annual_estimate_W25_W17
3 | 0.2 | 260 | 13.86 | 18.76 | annual_estimate_W25_W17
3 | 0.15 | 195 | 12.94 | 15.07 | annual_estimate_W25_W17
6 | 1 | 1300 | 73.2 | 17.76 | annual_estimate_W25_W17
6 | 0.9 | 1170 | 60.87 | 19.22 | annual_estimate_W25_W17
6 | 0.8 | 1040 | 48.31 | 21.52 | annual_estimate_W25_W17
6 | 0.7 | 910.2 | 36.73 | 24.77 | annual_estimate_W25_W17
6 | 0.6 | 780 | 28.62 | 27.26 | annual_estimate_W25_W17
6 | 0.5 | 649.9 | 22.36 | 29.07 | annual_estimate_W25_W17
6 | 0.4 | 520.1 | 18.07 | 28.78 | annual_estimate_W25_W17
6 | 0.3 | 390 | 16.26 | 23.99 | annual_estimate_W25_W17
6 | 0.2 | 260 | 14.06 | 18.49 | annual_estimate_W25_W17
6 | 0.15 | 195 | 12.92 | 15.09 | annual_estimate_W25_W17
9 | 1 | 1300 | 83.85 | 15.51 | annual_estimate_W25_W17
9 | 0.9 | 1170 | 71.03 | 16.47 | annual_estimate_W25_W17
9 | 0.8 | 1040 | 57.14 | 18.2 | annual_estimate_W25_W17
9 | 0.7 | 910.2 | 44.17 | 20.6 | annual_estimate_W25_W17
9 | 0.6 | 780 | 34.62 | 22.53 | annual_estimate_W25_W17
9 | 0.5 | 649.9 | 26.67 | 24.37 | annual_estimate_W25_W17
9 | 0.4 | 520.1 | 19.69 | 26.4 | annual_estimate_W25_W17
9 | 0.3 | 390 | 16.82 | 23.18 | annual_estimate_W25_W17
9 | 0.2 | 260 | 14.32 | 18.15 | annual_estimate_W25_W17
9 | 0.15 | 195 | 13.06 | 14.93 | annual_estimate_W25_W17
11 | 1 | 1300 | 92.56 | 14.05 | annual_estimate_W25_W17
11 | 0.9 | 1170 | 79.45 | 14.73 | annual_estimate_W25_W17
11 | 0.8 | 1040 | 64.74 | 16.07 | annual_estimate_W25_W17
11 | 0.7 | 910.2 | 51.59 | 17.64 | annual_estimate_W25_W17
11 | 0.6 | 780 | 39.76 | 19.63 | annual_estimate_W25_W17
11 | 0.5 | 649.9 | 30.14 | 21.56 | annual_estimate_W25_W17
11 | 0.4 | 520.1 | 22.24 | 23.38 | annual_estimate_W25_W17
11 | 0.3 | 390 | 17.55 | 22.23 | annual_estimate_W25_W17
11 | 0.2 | 260 | 14.8 | 17.57 | annual_estimate_W25_W17
11 | 0.15 | 195 | 13.2 | 14.77 | annual_estimate_W25_W17
14 | 1 | 1300 | 107.5 | 12.09 | annual_estimate_W25_W17
14 | 0.9 | 1170 | 94.44 | 12.39 | annual_estimate_W25_W17
14 | 0.8 | 1040 | 78.02 | 13.33 | annual_estimate_W25_W17
14 | 0.7 | 910.2 | 63.48 | 14.34 | annual_estimate_W25_W17
14 | 0.6 | 780 | 50.72 | 15.38 | annual_estimate_W25_W17
14 | 0.5 | 649.9 | 39.44 | 16.48 | annual_estimate_W25_W17
14 | 0.4 | 520.1 | 29.72 | 17.5 | annual_estimate_W25_W17
14 | 0.3 | 390 | 21.61 | 18.05 | annual_estimate_W25_W17
14 | 0.2 | 260 | 15.76 | 16.5 | annual_estimate_W25_W17
14 | 0.15 | 195 | 14.06 | 13.87 | annual_estimate_W25_W17
17 | 1 | 1300 | 124.9 | 10.41 | annual_estimate_W25_W17
17 | 0.9 | 1170 | 110.5 | 10.59 | annual_estimate_W25_W17
17 | 0.8 | 1040 | 92.69 | 11.22 | annual_estimate_W25_W17
17 | 0.7 | 910.2 | 76.4 | 11.91 | annual_estimate_W25_W17
17 | 0.6 | 780 | 62.02 | 12.58 | annual_estimate_W25_W17
17 | 0.5 | 649.9 | 49.46 | 13.14 | annual_estimate_W25_W17
17 | 0.4 | 520.1 | 38.54 | 13.49 | annual_estimate_W25_W17
17 | 0.3 | 390 | 29.28 | 13.32 | annual_estimate_W25_W17
17 | 0.2 | 260 | 21.09 | 12.33 | annual_estimate_W25_W17
17 | 0.15 | 195 | 17.58 | 11.09 | annual_estimate_W25_W17
20 | 1 | 1300 | 143.8 | 9.041 | annual_estimate_W25_W17
20 | 0.9 | 1170 | 127.8 | 9.154 | annual_estimate_W25_W17
20 | 0.8 | 1040 | 108.3 | 9.607 | annual_estimate_W25_W17
20 | 0.7 | 910.2 | 90.35 | 10.07 | annual_estimate_W25_W17
20 | 0.6 | 780 | 74.36 | 10.49 | annual_estimate_W25_W17
20 | 0.5 | 649.9 | 60.12 | 10.81 | annual_estimate_W25_W17
20 | 0.4 | 520.1 | 47.93 | 10.85 | annual_estimate_W25_W17
20 | 0.3 | 390 | 36.98 | 10.55 | annual_estimate_W25_W17
20 | 0.2 | 260 | 27.75 | 9.371 | annual_estimate_W25_W17
20 | 0.15 | 195 | 23.9 | 8.16 | annual_estimate_W25_W17
23 | 1 | 1300 | 164.1 | 7.923 | annual_estimate_W25_W17
23 | 0.9 | 1170 | 146.7 | 7.977 | annual_estimate_W25_W17
23 | 0.8 | 1040 | 125.3 | 8.301 | annual_estimate_W25_W17
23 | 0.7 | 910.2 | 105.6 | 8.618 | annual_estimate_W25_W17
23 | 0.6 | 780 | 87.8 | 8.884 | annual_estimate_W25_W17
23 | 0.5 | 649.9 | 72.01 | 9.027 | annual_estimate_W25_W17
23 | 0.4 | 520.1 | 58.07 | 8.956 | annual_estimate_W25_W17
23 | 0.3 | 390 | 45.86 | 8.505 | annual_estimate_W25_W17
23 | 0.2 | 260 | 35.7 | 7.283 | annual_estimate_W25_W17
23 | 0.15 | 195 | 31.22 | 6.247 | annual_estimate_W25_W17
25 | 1 | 1300 | 178.2 | 7.295 | annual_estimate_W25_W17
25 | 0.9 | 1170 | 159.8 | 7.323 | annual_estimate_W25_W17
25 | 0.8 | 1040 | 137.3 | 7.576 | annual_estimate_W25_W17
25 | 0.7 | 910.2 | 116.5 | 7.809 | annual_estimate_W25_W17
25 | 0.6 | 780 | 97.59 | 7.993 | annual_estimate_W25_W17
25 | 0.5 | 649.9 | 80.81 | 8.044 | annual_estimate_W25_W17
25 | 0.4 | 520.1 | 65.32 | 7.961 | annual_estimate_W25_W17
25 | 0.3 | 390 | 51.95 | 7.509 | annual_estimate_W25_W17
25 | 0.2 | 260 | 41.02 | 6.338 | annual_estimate_W25_W17
25 | 0.15 | 195 | 37.18 | 5.245 | annual_estimate_W25_W17
28 | 1 | 1300 | 201.8 | 6.441 | annual_estimate_W25_W17
28 | 0.9 | 1170 | 181.4 | 6.45 | annual_estimate_W25_W17
28 | 0.8 | 1040 | 156.9 | 6.63 | annual_estimate_W25_W17
28 | 0.7 | 910.2 | 134.3 | 6.775 | annual_estimate_W25_W17
28 | 0.6 | 780 | 113.7 | 6.86 | annual_estimate_W25_W17
28 | 0.5 | 649.9 | 95.33 | 6.819 | annual_estimate_W25_W17
28 | 0.4 | 520.1 | 78.95 | 6.586 | annual_estimate_W25_W17
28 | 0.3 | 390 | 64.53 | 6.044 | annual_estimate_W25_W17
28 | 0.2 | 260 | 53.21 | 4.887 | annual_estimate_W25_W17
28 | 0.15 | 195 | 52.03 | 3.748 | annual_estimate_W25_W17
31 | 1 | 1300 | 226.3 | 5.745 | annual_estimate_W25_W17
31 | 0.9 | 1170 | 205 | 5.708 | annual_estimate_W25_W17
31 | 0.8 | 1040 | 178.7 | 5.821 | annual_estimate_W25_W17
31 | 0.7 | 910.2 | 154.7 | 5.883 | annual_estimate_W25_W17
31 | 0.6 | 780 | 131.9 | 5.915 | annual_estimate_W25_W17
31 | 0.5 | 649.9 | 111.5 | 5.832 | annual_estimate_W25_W17
31 | 0.4 | 520.1 | 93.49 | 5.562 | annual_estimate_W25_W17
31 | 0.3 | 390 | 77.81 | 5.012 | annual_estimate_W25_W17
31 | 0.2 | 260 | 67.13 | 3.873 | annual_estimate_W25_W17
31 | 0.15 | 195 | 66.35 | 2.938 | annual_estimate_W25_W17
34 | 1 | 1300 | 254 | 5.118 | annual_estimate_W25_W17
34 | 0.9 | 1170 | 231.4 | 5.056 | annual_estimate_W25_W17
34 | 0.8 | 1040 | 202.7 | 5.13 | annual_estimate_W25_W17
34 | 0.7 | 910.2 | 175.5 | 5.184 | annual_estimate_W25_W17
34 | 0.6 | 780 | 151.4 | 5.153 | annual_estimate_W25_W17
34 | 0.5 | 649.9 | 129.3 | 5.026 | annual_estimate_W25_W17
34 | 0.4 | 520.1 | 109.8 | 4.738 | annual_estimate_W25_W17
34 | 0.3 | 390 | 91.72 | 4.252 | annual_estimate_W25_W17
34 | 0.2 | 260 | 80.73 | 3.221 | annual_estimate_W25_W17
34 | 0.15 | 195 | 81.25 | 2.401 | annual_estimate_W25_W17
36 | 1 | 1300 | 273.2 | 4.759 | annual_estimate_W25_W17
36 | 0.9 | 1170 | 249.9 | 4.682 | annual_estimate_W25_W17
36 | 0.8 | 1040 | 220.7 | 4.712 | annual_estimate_W25_W17
36 | 0.7 | 910.2 | 192.6 | 4.724 | annual_estimate_W25_W17
36 | 0.6 | 780 | 166.5 | 4.686 | annual_estimate_W25_W17
36 | 0.5 | 649.9 | 142.6 | 4.56 | annual_estimate_W25_W17
36 | 0.4 | 520.1 | 121.2 | 4.291 | annual_estimate_W25_W17
36 | 0.3 | 390 | 101.2 | 3.855 | annual_estimate_W25_W17
36 | 0.2 | 260 | 93.83 | 2.771 | annual_estimate_W25_W17
36 | 0.15 | 195 | 90.71 | 2.15 | annual_estimate_W25_W17
39 | 1 | 1300 | 305.4 | 4.257 | annual_estimate_W25_W17
39 | 0.9 | 1170 | 280.4 | 4.172 | annual_estimate_W25_W17
39 | 0.8 | 1040 | 246.9 | 4.212 | annual_estimate_W25_W17
39 | 0.7 | 910.2 | 216.7 | 4.199 | annual_estimate_W25_W17
39 | 0.6 | 780 | 190 | 4.105 | annual_estimate_W25_W17
39 | 0.5 | 649.9 | 164.7 | 3.948 | annual_estimate_W25_W17
39 | 0.4 | 520.1 | 142.4 | 3.651 | annual_estimate_W25_W17
39 | 0.3 | 390 | 123.2 | 3.166 | annual_estimate_W25_W17
39 | 0.2 | 260 | 109.6 | 2.372 | annual_estimate_W25_W17
39 | 0.15 | 195 | 103.9 | 1.876 | annual_estimate_W25_W17
42 | 1 | 1300 | 341.1 | 3.812 | annual_estimate_W25_W17
42 | 0.9 | 1170 | 313.7 | 3.729 | annual_estimate_W25_W17
42 | 0.8 | 1040 | 277.6 | 3.747 | annual_estimate_W25_W17
42 | 0.7 | 910.2 | 244.5 | 3.721 | annual_estimate_W25_W17
42 | 0.6 | 780 | 213.9 | 3.647 | annual_estimate_W25_W17
42 | 0.5 | 649.9 | 185.7 | 3.5 | annual_estimate_W25_W17
42 | 0.4 | 520.1 | 161.4 | 3.221 | annual_estimate_W25_W17
42 | 0.3 | 390 | 142.3 | 2.741 | annual_estimate_W25_W17
42 | 0.2 | 260 | 123 | 2.115 | annual_estimate_W25_W17
42 | 0.15 | 195 | 119.5 | 1.632 | annual_estimate_W25_W17
45 | 1 | 1300 | 380.4 | 3.418 | annual_estimate_W25_W17
45 | 0.9 | 1170 | 350.3 | 3.34 | annual_estimate_W25_W17
45 | 0.8 | 1040 | 312 | 3.334 | annual_estimate_W25_W17
45 | 0.7 | 910.2 | 274.6 | 3.315 | annual_estimate_W25_W17
45 | 0.6 | 780 | 240.2 | 3.247 | annual_estimate_W25_W17
45 | 0.5 | 649.9 | 208.9 | 3.112 | annual_estimate_W25_W17
45 | 0.4 | 520.1 | 181.6 | 2.864 | annual_estimate_W25_W17
45 | 0.3 | 390 | 158.6 | 2.459 | annual_estimate_W25_W17
45 | 0.2 | 260 | 139 | 1.87 | annual_estimate_W25_W17
45 | 0.15 | 195 | 146.2 | 1.334 | annual_estimate_W25_W17

## Condenser_Performance
percent_load | load_ratio | ambient_C | heat_rejection_kW | discharge_air_temp_C | total_air_flow_m3_s | active_fans | source_document | source_page | source_range
100 | 1 | 46.1 | 1724.2 |  | 140 | 20 | 01 YVAM1500 PG25 1300kW Performance Report Rev A.PDF | Page 2 | Design point
60 | 0.6 | 38 | 1113 | 44.94 | 137 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 48 | 1002 | 54.06 | 140 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 46 | 986.4 | 52.06 | 138 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 44 | 971.3 | 50.06 | 136 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 42 | 954.3 | 48.17 | 131 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 40 | 941.4 | 46.28 | 128 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 38 | 927.4 | 44.17 | 128 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
100 | 1 | 55 | 1708 | 61.89 | 207 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 54 | 1697 | 61.17 | 198 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 53 | 1690 | 60.61 | 186 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 52 | 1678 | 59.72 | 182 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 51 | 1664 | 58.78 | 181 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 50 | 1651 | 57.78 | 179 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 49 | 1638 | 56.78 | 178 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 55 | 1548 | 62.17 | 180 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 54 | 1535 | 61.22 | 179 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 53 | 1525 | 60.44 | 172 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 52 | 1511 | 59.39 | 173 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 51 | 1499 | 58.39 | 171 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 50 | 1485 | 57.28 | 172 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 49 | 1475 | 56.39 | 168 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 55 | 1379 | 61.78 | 170 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 54 | 1368 | 60.89 | 166 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 53 | 1355 | 59.83 | 167 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 52 | 1344 | 58.83 | 166 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 51 | 1335 | 58.06 | 160 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 50 | 1322 | 56.94 | 161 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 49 | 1311 | 55.89 | 161 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 55 | 1213 | 61.44 | 158 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 54 | 1202 | 60.44 | 156 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 53 | 1191 | 59.39 | 157 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 52 | 1179 | 58.28 | 158 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 51 | 1169 | 57.39 | 155 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 50 | 1162 | 56.72 | 147 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 49 | 1151 | 55.5 | 150 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 55 | 1048 | 60.89 | 150 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 54 | 1038 | 59.89 | 148 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 53 | 1029 | 58.94 | 145 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 52 | 1018 | 57.78 | 148 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 51 | 1008 | 56.83 | 147 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 50 | 1000 | 55.83 | 145 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 49 | 992.1 | 54.89 | 142 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
50 | 0.5 | 55 | 885.2 | 60.22 | 143 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 54 | 877.1 | 59.33 | 138 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 53 | 867.7 | 58.28 | 139 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 52 | 858.6 | 57.22 | 139 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 51 | 851.7 | 56.39 | 134 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 50 | 844.9 | 55.39 | 133 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 49 | 837 | 54.39 | 132 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 55 | 726.8 | 59.44 | 138 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 54 | 720.4 | 58.78 | 127 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 53 | 712.5 | 57.78 | 127 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 52 | 705.1 | 56.72 | 126 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 51 | 698.9 | 55.83 | 122 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 50 | 695.6 | 55.33 | 111 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 49 | 685.7 | 53.78 | 123 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C

## Validation
Item | Value
Formula errors scan | Pass
Model | YVAM1500
Design capacity | 1300 kW
Combined ambient points | -5, -3, 0, 3, 6, 9, 11, 14, 17, 20, 23, 25, 28, 31, 34, 36, 39, 42, 45, 46.1°C
Combined load points | 100%, 90%, 80%, 70%, 60%, 50%, 40%, 30%, 20%, 15%
Solver rows | 191
PDF design point | 100% / 46.1°C / 1300 kW / 424.2 kW / COP 3.064
Priority rule | PDF design point overrides annual workbook at identical condition
Recommended solver behavior | Use 2D interpolation within available grid; clamp only outside the source range.
Do not double count | power_input_kW is total unit input power; PDF states fan and auxiliary power are included.
Source limitation | Most off-design points come from the annual estimate workbook, not the supplied certified PDF.
Production note | Run frontend verification before replacing the active ACC workbook.

## Solver_Curve_Original
ambient_C | load_ratio | capacity_kW | power_input_kW | unit_efficiency_kW_per_kW | source_range
-5 | 1 | 1300 | 58.36 | 22.27 | annual_estimate_W25_W17
-5 | 0.9 | 1170 | 47.34 | 24.72 | annual_estimate_W25_W17
-5 | 0.8 | 1040 | 35.32 | 29.46 | annual_estimate_W25_W17
-5 | 0.7 | 910.2 | 27.42 | 33.18 | annual_estimate_W25_W17
-5 | 0.6 | 780 | 22.53 | 34.62 | annual_estimate_W25_W17
-5 | 0.5 | 649.9 | 18.42 | 35.29 | annual_estimate_W25_W17
-5 | 0.4 | 520.1 | 16.48 | 31.57 | annual_estimate_W25_W17
-5 | 0.3 | 390 | 15.83 | 24.63 | annual_estimate_W25_W17
-5 | 0.2 | 260 | 13.93 | 18.67 | annual_estimate_W25_W17
-5 | 0.15 | 195 | 12.77 | 15.27 | annual_estimate_W25_W17
-3 | 1 | 1300 | 59.26 | 21.94 | annual_estimate_W25_W17
-3 | 0.9 | 1170 | 48.18 | 24.29 | annual_estimate_W25_W17
-3 | 0.8 | 1040 | 35.88 | 28.99 | annual_estimate_W25_W17
-3 | 0.7 | 910.2 | 27.75 | 32.81 | annual_estimate_W25_W17
-3 | 0.6 | 780 | 22.48 | 34.68 | annual_estimate_W25_W17
-3 | 0.5 | 649.9 | 18.27 | 35.59 | annual_estimate_W25_W17
-3 | 0.4 | 520.1 | 16.58 | 31.35 | annual_estimate_W25_W17
-3 | 0.3 | 390 | 15.94 | 24.47 | annual_estimate_W25_W17
-3 | 0.2 | 260 | 13.81 | 18.83 | annual_estimate_W25_W17
-3 | 0.15 | 195 | 12.78 | 15.25 | annual_estimate_W25_W17
0 | 1 | 1300 | 62.43 | 20.82 | annual_estimate_W25_W17
0 | 0.9 | 1170 | 50.62 | 23.11 | annual_estimate_W25_W17
0 | 0.8 | 1040 | 37.73 | 27.56 | annual_estimate_W25_W17
0 | 0.7 | 910.2 | 28.92 | 31.46 | annual_estimate_W25_W17
0 | 0.6 | 780 | 22.52 | 34.62 | annual_estimate_W25_W17
0 | 0.5 | 649.9 | 18.53 | 35.1 | annual_estimate_W25_W17
0 | 0.4 | 520.1 | 16.79 | 30.96 | annual_estimate_W25_W17
0 | 0.3 | 390 | 15.96 | 24.42 | annual_estimate_W25_W17
0 | 0.2 | 260 | 14.28 | 18.21 | annual_estimate_W25_W17
0 | 0.15 | 195 | 13.34 | 14.61 | annual_estimate_W25_W17
3 | 1 | 1300 | 66.47 | 19.56 | annual_estimate_W25_W17
3 | 0.9 | 1170 | 54.89 | 21.32 | annual_estimate_W25_W17
3 | 0.8 | 1040 | 41.71 | 24.94 | annual_estimate_W25_W17
3 | 0.7 | 910.2 | 32.1 | 28.34 | annual_estimate_W25_W17
3 | 0.6 | 780 | 25.37 | 30.74 | annual_estimate_W25_W17
3 | 0.5 | 649.9 | 20.45 | 31.77 | annual_estimate_W25_W17
3 | 0.4 | 520.1 | 17.65 | 29.46 | annual_estimate_W25_W17
3 | 0.3 | 390 | 16.33 | 23.88 | annual_estimate_W25_W17
3 | 0.2 | 260 | 13.86 | 18.76 | annual_estimate_W25_W17
3 | 0.15 | 195 | 12.94 | 15.07 | annual_estimate_W25_W17
6 | 1 | 1300 | 73.2 | 17.76 | annual_estimate_W25_W17
6 | 0.9 | 1170 | 60.87 | 19.22 | annual_estimate_W25_W17
6 | 0.8 | 1040 | 48.31 | 21.52 | annual_estimate_W25_W17
6 | 0.7 | 910.2 | 36.73 | 24.77 | annual_estimate_W25_W17
6 | 0.6 | 780 | 28.62 | 27.26 | annual_estimate_W25_W17
6 | 0.5 | 649.9 | 22.36 | 29.07 | annual_estimate_W25_W17
6 | 0.4 | 520.1 | 18.07 | 28.78 | annual_estimate_W25_W17
6 | 0.3 | 390 | 16.26 | 23.99 | annual_estimate_W25_W17
6 | 0.2 | 260 | 14.06 | 18.49 | annual_estimate_W25_W17
6 | 0.15 | 195 | 12.92 | 15.09 | annual_estimate_W25_W17
9 | 1 | 1300 | 83.85 | 15.51 | annual_estimate_W25_W17
9 | 0.9 | 1170 | 71.03 | 16.47 | annual_estimate_W25_W17
9 | 0.8 | 1040 | 57.14 | 18.2 | annual_estimate_W25_W17
9 | 0.7 | 910.2 | 44.17 | 20.6 | annual_estimate_W25_W17
9 | 0.6 | 780 | 34.62 | 22.53 | annual_estimate_W25_W17
9 | 0.5 | 649.9 | 26.67 | 24.37 | annual_estimate_W25_W17
9 | 0.4 | 520.1 | 19.69 | 26.4 | annual_estimate_W25_W17
9 | 0.3 | 390 | 16.82 | 23.18 | annual_estimate_W25_W17
9 | 0.2 | 260 | 14.32 | 18.15 | annual_estimate_W25_W17
9 | 0.15 | 195 | 13.06 | 14.93 | annual_estimate_W25_W17
11 | 1 | 1300 | 92.56 | 14.05 | annual_estimate_W25_W17
11 | 0.9 | 1170 | 79.45 | 14.73 | annual_estimate_W25_W17
11 | 0.8 | 1040 | 64.74 | 16.07 | annual_estimate_W25_W17
11 | 0.7 | 910.2 | 51.59 | 17.64 | annual_estimate_W25_W17
11 | 0.6 | 780 | 39.76 | 19.63 | annual_estimate_W25_W17
11 | 0.5 | 649.9 | 30.14 | 21.56 | annual_estimate_W25_W17
11 | 0.4 | 520.1 | 22.24 | 23.38 | annual_estimate_W25_W17
11 | 0.3 | 390 | 17.55 | 22.23 | annual_estimate_W25_W17
11 | 0.2 | 260 | 14.8 | 17.57 | annual_estimate_W25_W17
11 | 0.15 | 195 | 13.2 | 14.77 | annual_estimate_W25_W17
14 | 1 | 1300 | 107.5 | 12.09 | annual_estimate_W25_W17
14 | 0.9 | 1170 | 94.44 | 12.39 | annual_estimate_W25_W17
14 | 0.8 | 1040 | 78.02 | 13.33 | annual_estimate_W25_W17
14 | 0.7 | 910.2 | 63.48 | 14.34 | annual_estimate_W25_W17
14 | 0.6 | 780 | 50.72 | 15.38 | annual_estimate_W25_W17
14 | 0.5 | 649.9 | 39.44 | 16.48 | annual_estimate_W25_W17
14 | 0.4 | 520.1 | 29.72 | 17.5 | annual_estimate_W25_W17
14 | 0.3 | 390 | 21.61 | 18.05 | annual_estimate_W25_W17
14 | 0.2 | 260 | 15.76 | 16.5 | annual_estimate_W25_W17
14 | 0.15 | 195 | 14.06 | 13.87 | annual_estimate_W25_W17
17 | 1 | 1300 | 124.9 | 10.41 | annual_estimate_W25_W17
17 | 0.9 | 1170 | 110.5 | 10.59 | annual_estimate_W25_W17
17 | 0.8 | 1040 | 92.69 | 11.22 | annual_estimate_W25_W17
17 | 0.7 | 910.2 | 76.4 | 11.91 | annual_estimate_W25_W17
17 | 0.6 | 780 | 62.02 | 12.58 | annual_estimate_W25_W17
17 | 0.5 | 649.9 | 49.46 | 13.14 | annual_estimate_W25_W17
17 | 0.4 | 520.1 | 38.54 | 13.49 | annual_estimate_W25_W17
17 | 0.3 | 390 | 29.28 | 13.32 | annual_estimate_W25_W17
17 | 0.2 | 260 | 21.09 | 12.33 | annual_estimate_W25_W17
17 | 0.15 | 195 | 17.58 | 11.09 | annual_estimate_W25_W17
20 | 1 | 1300 | 143.8 | 9.041 | annual_estimate_W25_W17
20 | 0.9 | 1170 | 127.8 | 9.154 | annual_estimate_W25_W17
20 | 0.8 | 1040 | 108.3 | 9.607 | annual_estimate_W25_W17
20 | 0.7 | 910.2 | 90.35 | 10.07 | annual_estimate_W25_W17
20 | 0.6 | 780 | 74.36 | 10.49 | annual_estimate_W25_W17
20 | 0.5 | 649.9 | 60.12 | 10.81 | annual_estimate_W25_W17
20 | 0.4 | 520.1 | 47.93 | 10.85 | annual_estimate_W25_W17
20 | 0.3 | 390 | 36.98 | 10.55 | annual_estimate_W25_W17
20 | 0.2 | 260 | 27.75 | 9.371 | annual_estimate_W25_W17
20 | 0.15 | 195 | 23.9 | 8.16 | annual_estimate_W25_W17
23 | 1 | 1300 | 164.1 | 7.923 | annual_estimate_W25_W17
23 | 0.9 | 1170 | 146.7 | 7.977 | annual_estimate_W25_W17
23 | 0.8 | 1040 | 125.3 | 8.301 | annual_estimate_W25_W17
23 | 0.7 | 910.2 | 105.6 | 8.618 | annual_estimate_W25_W17
23 | 0.6 | 780 | 87.8 | 8.884 | annual_estimate_W25_W17
23 | 0.5 | 649.9 | 72.01 | 9.027 | annual_estimate_W25_W17
23 | 0.4 | 520.1 | 58.07 | 8.956 | annual_estimate_W25_W17
23 | 0.3 | 390 | 45.86 | 8.505 | annual_estimate_W25_W17
23 | 0.2 | 260 | 35.7 | 7.283 | annual_estimate_W25_W17
23 | 0.15 | 195 | 31.22 | 6.247 | annual_estimate_W25_W17
25 | 1 | 1300 | 178.2 | 7.295 | annual_estimate_W25_W17
25 | 0.9 | 1170 | 159.8 | 7.323 | annual_estimate_W25_W17
25 | 0.8 | 1040 | 137.3 | 7.576 | annual_estimate_W25_W17
25 | 0.7 | 910.2 | 116.5 | 7.809 | annual_estimate_W25_W17
25 | 0.6 | 780 | 97.59 | 7.993 | annual_estimate_W25_W17
25 | 0.5 | 649.9 | 80.81 | 8.044 | annual_estimate_W25_W17
25 | 0.4 | 520.1 | 65.32 | 7.961 | annual_estimate_W25_W17
25 | 0.3 | 390 | 51.95 | 7.509 | annual_estimate_W25_W17
25 | 0.2 | 260 | 41.02 | 6.338 | annual_estimate_W25_W17
25 | 0.15 | 195 | 37.18 | 5.245 | annual_estimate_W25_W17
28 | 1 | 1300 | 201.8 | 6.441 | annual_estimate_W25_W17
28 | 0.9 | 1170 | 181.4 | 6.45 | annual_estimate_W25_W17
28 | 0.8 | 1040 | 156.9 | 6.63 | annual_estimate_W25_W17
28 | 0.7 | 910.2 | 134.3 | 6.775 | annual_estimate_W25_W17
28 | 0.6 | 780 | 113.7 | 6.86 | annual_estimate_W25_W17
28 | 0.5 | 649.9 | 95.33 | 6.819 | annual_estimate_W25_W17
28 | 0.4 | 520.1 | 78.95 | 6.586 | annual_estimate_W25_W17
28 | 0.3 | 390 | 64.53 | 6.044 | annual_estimate_W25_W17
28 | 0.2 | 260 | 53.21 | 4.887 | annual_estimate_W25_W17
28 | 0.15 | 195 | 52.03 | 3.748 | annual_estimate_W25_W17
31 | 1 | 1300 | 226.3 | 5.745 | annual_estimate_W25_W17
31 | 0.9 | 1170 | 205 | 5.708 | annual_estimate_W25_W17
31 | 0.8 | 1040 | 178.7 | 5.821 | annual_estimate_W25_W17
31 | 0.7 | 910.2 | 154.7 | 5.883 | annual_estimate_W25_W17
31 | 0.6 | 780 | 131.9 | 5.915 | annual_estimate_W25_W17
31 | 0.5 | 649.9 | 111.5 | 5.832 | annual_estimate_W25_W17
31 | 0.4 | 520.1 | 93.49 | 5.562 | annual_estimate_W25_W17
31 | 0.3 | 390 | 77.81 | 5.012 | annual_estimate_W25_W17
31 | 0.2 | 260 | 67.13 | 3.873 | annual_estimate_W25_W17
31 | 0.15 | 195 | 66.35 | 2.938 | annual_estimate_W25_W17
34 | 1 | 1300 | 254 | 5.118 | annual_estimate_W25_W17
34 | 0.9 | 1170 | 231.4 | 5.056 | annual_estimate_W25_W17
34 | 0.8 | 1040 | 202.7 | 5.13 | annual_estimate_W25_W17
34 | 0.7 | 910.2 | 175.5 | 5.184 | annual_estimate_W25_W17
34 | 0.6 | 780 | 151.4 | 5.153 | annual_estimate_W25_W17
34 | 0.5 | 649.9 | 129.3 | 5.026 | annual_estimate_W25_W17
34 | 0.4 | 520.1 | 109.8 | 4.738 | annual_estimate_W25_W17
34 | 0.3 | 390 | 91.72 | 4.252 | annual_estimate_W25_W17
34 | 0.2 | 260 | 80.73 | 3.221 | annual_estimate_W25_W17
34 | 0.15 | 195 | 81.25 | 2.401 | annual_estimate_W25_W17
36 | 1 | 1300 | 273.2 | 4.759 | annual_estimate_W25_W17
36 | 0.9 | 1170 | 249.9 | 4.682 | annual_estimate_W25_W17
36 | 0.8 | 1040 | 220.7 | 4.712 | annual_estimate_W25_W17
36 | 0.7 | 910.2 | 192.6 | 4.724 | annual_estimate_W25_W17
36 | 0.6 | 780 | 166.5 | 4.686 | annual_estimate_W25_W17
36 | 0.5 | 649.9 | 142.6 | 4.56 | annual_estimate_W25_W17
36 | 0.4 | 520.1 | 121.2 | 4.291 | annual_estimate_W25_W17
36 | 0.3 | 390 | 101.2 | 3.855 | annual_estimate_W25_W17
36 | 0.2 | 260 | 93.83 | 2.771 | annual_estimate_W25_W17
36 | 0.15 | 195 | 90.71 | 2.15 | annual_estimate_W25_W17
39 | 1 | 1300 | 305.4 | 4.257 | annual_estimate_W25_W17
39 | 0.9 | 1170 | 280.4 | 4.172 | annual_estimate_W25_W17
39 | 0.8 | 1040 | 246.9 | 4.212 | annual_estimate_W25_W17
39 | 0.7 | 910.2 | 216.7 | 4.199 | annual_estimate_W25_W17
39 | 0.6 | 780 | 190 | 4.105 | annual_estimate_W25_W17
39 | 0.5 | 649.9 | 164.7 | 3.948 | annual_estimate_W25_W17
39 | 0.4 | 520.1 | 142.4 | 3.651 | annual_estimate_W25_W17
39 | 0.3 | 390 | 123.2 | 3.166 | annual_estimate_W25_W17
39 | 0.2 | 260 | 109.6 | 2.372 | annual_estimate_W25_W17
39 | 0.15 | 195 | 103.9 | 1.876 | annual_estimate_W25_W17
42 | 1 | 1300 | 341.1 | 3.812 | annual_estimate_W25_W17
42 | 0.9 | 1170 | 313.7 | 3.729 | annual_estimate_W25_W17
42 | 0.8 | 1040 | 277.6 | 3.747 | annual_estimate_W25_W17
42 | 0.7 | 910.2 | 244.5 | 3.721 | annual_estimate_W25_W17
42 | 0.6 | 780 | 213.9 | 3.647 | annual_estimate_W25_W17
42 | 0.5 | 649.9 | 185.7 | 3.5 | annual_estimate_W25_W17
42 | 0.4 | 520.1 | 161.4 | 3.221 | annual_estimate_W25_W17
42 | 0.3 | 390 | 142.3 | 2.741 | annual_estimate_W25_W17
42 | 0.2 | 260 | 123 | 2.115 | annual_estimate_W25_W17
42 | 0.15 | 195 | 119.5 | 1.632 | annual_estimate_W25_W17
45 | 1 | 1300 | 380.4 | 3.418 | annual_estimate_W25_W17
45 | 0.9 | 1170 | 350.3 | 3.34 | annual_estimate_W25_W17
45 | 0.8 | 1040 | 312 | 3.334 | annual_estimate_W25_W17
45 | 0.7 | 910.2 | 274.6 | 3.315 | annual_estimate_W25_W17
45 | 0.6 | 780 | 240.2 | 3.247 | annual_estimate_W25_W17
45 | 0.5 | 649.9 | 208.9 | 3.112 | annual_estimate_W25_W17
45 | 0.4 | 520.1 | 181.6 | 2.864 | annual_estimate_W25_W17
45 | 0.3 | 390 | 158.6 | 2.459 | annual_estimate_W25_W17
45 | 0.2 | 260 | 139 | 1.87 | annual_estimate_W25_W17
45 | 0.15 | 195 | 146.2 | 1.334 | annual_estimate_W25_W17
46.1 | 1 | 1300 | 424.2 | 3.064 | pdf_design_point

## Low_Ambient_Notes
ACC_3 Solver_Curve Source Notes
Purpose | Provide a software-readable YVAM1500 ambient-temperature × load-ratio performance curve using the ACC_2 workbook structure.
Primary source | 003 Annual kWh workbook, sheet YVAM chiller load reference, W25/W17 condition.
Certified anchor | The PDF design point at 100% load and 46.1°C uses 1300 kW capacity, 424.2 kW total input, COP 3.064.
Priority | The PDF value replaces the annual workbook value at the identical 100% / 46.1°C point.
Data status | Other curve points are annual estimate values and should not be described as PDF-certified.
Interpolation | Use bilinear interpolation where a complete surrounding grid exists.
Irregular top point | 46.1°C exists only at 100% load; other load ratios extend to 45°C.
Outside range | Clamp or return a diagnostic outside -5°C to 46.1°C and 15% to 100% load.