## Information
Parameter | Value | Unit | Source
Equipment Type | CDU | - | Configuration
Model ID | CDU_1 | - | Configuration
Configuration | ACC_1MW_GRID_CDU | - | Configuration
Maximum Power | 15 | kW | Engineering Assumption
Base Power | 3.75 | kW | 25% of maximum power
Control Mode | Base Power + Quadratic Load Curve | - | Engineering Model
Curve Formula | P = 3.75 + (15 - 3.75) × load_ratio² | - | Engineering Model
Load Ratio Range | 0.10 - 1.00 | - | Software Lookup
Primary Read Sheet | Solver_Curve | - | PUE Solver
Notes | CDU total power includes fixed controls/auxiliaries plus variable pump power. | - | Engineering
Data Status | Estimated curve; replace with vendor curve when available. | - | Engineering

## Metadata
Item | Value
Version | v2.0
Status | Engineering Estimated Curve
Author | ChatGPT
Data Source | Engineering assumption based on CDU fixed auxiliary power and variable pump power
Maximum Power | 15 kW
Base Power | 3.75 kW
Curve Type | Quadratic with base power
Formula | P=3.75+(15-3.75)×L²
Validation | Pending vendor performance data

## Performance_Map
load_ratio | base_power_kW | variable_power_kW | total_power_kW | curve_basis | notes
0.1 | 3.75 | 0.11 | 3.86 | P=3.75+(15-3.75)×L² | Minimum modeled load point
0.15 | 3.75 | 0.25 | 4 | P=3.75+(15-3.75)×L² | Interpolated engineering point
0.2 | 3.75 | 0.45 | 4.2 | P=3.75+(15-3.75)×L² | Interpolated engineering point
0.25 | 3.75 | 0.7 | 4.45 | P=3.75+(15-3.75)×L² | Interpolated engineering point
0.3 | 3.75 | 1.01 | 4.76 | P=3.75+(15-3.75)×L² | Interpolated engineering point
0.35 | 3.75 | 1.38 | 5.13 | P=3.75+(15-3.75)×L² | Interpolated engineering point
0.4 | 3.75 | 1.8 | 5.55 | P=3.75+(15-3.75)×L² | Interpolated engineering point
0.5 | 3.75 | 2.81 | 6.56 | P=3.75+(15-3.75)×L² | Interpolated engineering point
0.6 | 3.75 | 4.05 | 7.8 | P=3.75+(15-3.75)×L² | Interpolated engineering point
0.7 | 3.75 | 5.51 | 9.26 | P=3.75+(15-3.75)×L² | Interpolated engineering point
0.8 | 3.75 | 7.2 | 10.95 | P=3.75+(15-3.75)×L² | Interpolated engineering point
0.9 | 3.75 | 9.11 | 12.86 | P=3.75+(15-3.75)×L² | Interpolated engineering point
1 | 3.75 | 11.25 | 15 | P=3.75+(15-3.75)×L² | Maximum power point

## Solver_Curve
load_ratio | power_kW
0.1 | 3.86
0.15 | 4
0.2 | 4.2
0.25 | 4.45
0.3 | 4.76
0.35 | 5.13
0.4 | 5.55
0.5 | 6.56
0.6 | 7.8
0.7 | 9.26
0.8 | 10.95
0.9 | 12.86
1 | 15

## Validation
Item | Value
Curve Type | Base Power + Quadratic
Maximum Power | 15 kW at load_ratio = 1.00
Base Power | 3.75 kW
Base Power Fraction | 25% of maximum power
Formula | P=3.75+(15-3.75)×L²
Load Ratio Range | 0.10 - 1.00
Monotonic Increase | PASS
Maximum Point Check | PASS: 15.00 kW
Formula Errors | PASS
Validation Status | Engineering estimate
Future Update | Replace with vendor CDU power curve when available