## Information
Parameter | Value | Unit | Source
Equipment Type | CDU | - | Configuration
Model ID | CDU_3 | - | Configuration
Configuration | CHILLER_DRYCOOLER_2MW_GASENGINE_CDU | - | Configuration
Maximum Power | 30 | kW | Engineering Assumption
Base Power | 7.5 | kW | 25% of maximum power
Control Mode | Base Power + Quadratic Load Curve | - | Engineering Model
Curve Formula | P = 7.5 + (30 - 7.5) × load_ratio² | - | Engineering Model
Load Ratio Range | 0.10 - 1.00 | - | Software Lookup
Primary Read Sheet | Solver_Curve | - | PUE Solver
Notes | CDU total power includes fixed controls/auxiliaries plus variable pump power. | - | Engineering
Data Status | Estimated curve; replace with vendor curve when available. | - | Engineering

## Metadata
Item | Value
Version | v2.0
Status | Engineering Estimated Curve
Author | ChatGPT
Data Source | Engineering assumption based on CDU fixed auxiliary power and variable pump power
Maximum Power | 30 kW
Base Power | 7.5 kW
Curve Type | Quadratic with base power
Formula | P=7.5+(30-7.5)×L²
Validation | Pending vendor performance data

## Performance_Map
load_ratio | base_power_kW | variable_power_kW | total_power_kW | curve_basis | notes
0.1 | 7.5 | 0.22 | 7.72 | P=7.5+(30-7.5)×L² | Engineering curve point
0.15 | 7.5 | 0.51 | 8.01 | P=7.5+(30-7.5)×L² | Engineering curve point
0.2 | 7.5 | 0.9 | 8.4 | P=7.5+(30-7.5)×L² | Engineering curve point
0.25 | 7.5 | 1.41 | 8.91 | P=7.5+(30-7.5)×L² | Engineering curve point
0.3 | 7.5 | 2.03 | 9.53 | P=7.5+(30-7.5)×L² | Engineering curve point
0.35 | 7.5 | 2.76 | 10.26 | P=7.5+(30-7.5)×L² | Engineering curve point
0.4 | 7.5 | 3.6 | 11.1 | P=7.5+(30-7.5)×L² | Engineering curve point
0.5 | 7.5 | 5.62 | 13.12 | P=7.5+(30-7.5)×L² | Engineering curve point
0.6 | 7.5 | 8.1 | 15.6 | P=7.5+(30-7.5)×L² | Engineering curve point
0.7 | 7.5 | 11.02 | 18.52 | P=7.5+(30-7.5)×L² | Engineering curve point
0.8 | 7.5 | 14.4 | 21.9 | P=7.5+(30-7.5)×L² | Engineering curve point
0.9 | 7.5 | 18.23 | 25.73 | P=7.5+(30-7.5)×L² | Engineering curve point
1 | 7.5 | 22.5 | 30 | P=7.5+(30-7.5)×L² | Maximum power point

## Solver_Curve
load_ratio | power_kW
0.1 | 7.72
0.15 | 8.01
0.2 | 8.4
0.25 | 8.91
0.3 | 9.53
0.35 | 10.26
0.4 | 11.1
0.5 | 13.12
0.6 | 15.6
0.7 | 18.52
0.8 | 21.9
0.9 | 25.73
1 | 30

## Validation
Item | Value
Curve Type | Base Power + Quadratic
Maximum Power | 30 kW at load_ratio = 1.00
Base Power | 7.5 kW
Base Power Fraction | 25% of maximum power
Formula | P=7.5+(30-7.5)×L²
Load Ratio Range | 0.10 - 1.00
Monotonic Increase | PASS
Maximum Point Check | PASS: 30.00 kW
Formula Errors | PASS
Validation Status | Engineering estimate
Future Update | Replace with vendor CDU power curve when available