## Information
Parameter | Value | Unit | Source
Equipment Type | Engine Radiator | - | Configuration
Equipment ID | ENGINE_RADIATOR_1 | - | Configuration Library
Control Strategy | Single Solver Curve | - | Engineering Model
Rated Maximum Power | 48 | kW | Engineering Assumption
Base Power | 12 | kW | 25% of maximum power
Load Ratio Basis | Engine Output / Rated Engine Output | - | Same philosophy as CW Pump
Curve Type | Base Power + Cubic Affinity Curve | - | Axial Fan Approximation
Formula | P = Pbase + (Pmax-Pbase) × Load Ratio³ | - | Engineering Model

## Metadata
Item | Value
Version | v1.0
Equipment | ENGINE_RADIATOR_1
Maximum Fan Power | 48 kW
Curve Model | Cubic fan affinity with base power
Load Ratio | Engine output ratio

## Performance_Map
load_ratio | base_power_kW | variable_power_kW | total_power_kW | curve_basis
0.1 | 12 | 0.04 | 12.04 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.15 | 12 | 0.12 | 12.12 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.2 | 12 | 0.29 | 12.29 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.25 | 12 | 0.56 | 12.56 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.3 | 12 | 0.97 | 12.97 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.35 | 12 | 1.54 | 13.54 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.4 | 12 | 2.3 | 14.3 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.5 | 12 | 4.5 | 16.5 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.6 | 12 | 7.78 | 19.78 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.7 | 12 | 12.35 | 24.35 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.8 | 12 | 18.43 | 30.43 | P=Pbase+(Pmax-Pbase)*load_ratio^3
0.9 | 12 | 26.24 | 38.24 | P=Pbase+(Pmax-Pbase)*load_ratio^3
1 | 12 | 36 | 48 | P=Pbase+(Pmax-Pbase)*load_ratio^3

## Solver_Curve
load_ratio | power_kW
0.1 | 12.04
0.15 | 12.12
0.2 | 12.29
0.25 | 12.56
0.3 | 12.97
0.35 | 13.54
0.4 | 14.3
0.5 | 16.5
0.6 | 19.78
0.7 | 24.35
0.8 | 30.43
0.9 | 38.24
1 | 48

## Validation
Item | Value
Curve Structure | Single Solver_Curve
Normal / Failure | Same curve
Maximum Power Check | 48 kW @ load_ratio=1.0
Formula | P=12+(48-12)*load_ratio^3