## Information
Parameter | Value | Unit | Source
Equipment Type | RTC | - | Configuration
Model ID | RTC_2MW | - | Configuration Naming Standard
Configuration | Cooling Unit 2 MW | - | Configuration Library
Control Mode | IT Load Ratio Curve | - | Engineering Fit
Reference IT Load | 2000 | kW | Engineering Assumption
Reference RTC Cooling | 200 | kW | Engineering Assumption
Maximum RTC Fan Power | 16 | kW | Engineering Assumption
Low-Load Flat Anchor Ratio | 0.4 | IT Load Ratio | Leadership Review
Fan Power at 40% Anchor | 4 | kW | Engineering Assumption
Fan Power at 10% Low Load | 3.68 | kW | Engineering Assumption
High-Load Curve Exponent | 2 | - | Engineering Fit
Formula Below 40% | Near-flat interpolation from 3.68 kW @10% to 4.00 kW @40% | - | Engineering Fit
Formula Above 40% | P = 4 + (16 - 4) * ((x - 0.40) / (1 - 0.40))^2 | - | Engineering Fit
Notes | RTC fan power curve scaled from the reviewed 20 kW reference shape to 16 kW maximum for a 2 MW cooling unit. | - | Engineering

## Metadata
Item | Value
Version | v1.2
Status | Preliminary Engineering Fit
Author | ChatGPT
Data Source | Engineering curve scaled from reviewed 20 kW RTC reference for 2 MW cooling unit
Validation | Pending vendor performance curve / field test data
Model Scope | RTC fan power curve for 2 MW cooling unit in PUE Solver
Applicable Range | IT Load Ratio 0.10 to 1.00
Curve Intent | Keep RTC fan power nearly flat below 40% IT load ratio
Caution | Do not treat RTC cooling reduction as linear fan power reduction

## Performance_Map
IT_Load_Ratio | RTC_Cooling_kW | Airflow_Ratio | RTC_Fan_Power_kW | Formula_Basis | Notes
0.1 | 20 | 0.1 | 3.68 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.15 | 30 | 0.15 | 3.74 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.2 | 40 | 0.2 | 3.78 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.25 | 50 | 0.25 | 3.84 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.3 | 60 | 0.3 | 3.9 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.35 | 70 | 0.35 | 3.94 | Scaled low-load near-flat interpolation | Near-flat low-load region
0.4 | 80 | 0.4 | 4 | Scaled low-load near-flat interpolation | Flat anchor at 40%
0.5 | 100 | 0.5 | 4.34 | P=4+(16-4)* ((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.6 | 120 | 0.6 | 5.34 | P=4+(16-4)* ((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.7 | 140 | 0.7 | 7 | P=4+(16-4)* ((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.8 | 160 | 0.8 | 9.34 | P=4+(16-4)* ((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.9 | 180 | 0.9 | 12.34 | P=4+(16-4)* ((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
1 | 200 | 1 | 16 | P=4+(16-4)* ((x-0.40)/(1-0.40))^2 | Maximum power at 100% reference load

## Solver_Curve
load_ratio | power_kW
0.1 | 3.68
0.15 | 3.74
0.2 | 3.78
0.25 | 3.84
0.3 | 3.9
0.35 | 3.94
0.4 | 4
0.5 | 4.34
0.6 | 5.34
0.7 | 7
0.8 | 9.34
0.9 | 12.34
1 | 16

## Validation
Item | Value
Curve Type | Near-flat low-load RTC fan curve
Validation Status | Preliminary
Maximum Power | 16 kW at 100% IT Load Ratio
Flat Region Intent | Below 40% IT Load Ratio, fan power changes only slightly
40% Anchor | 4.00 kW
10% Low-Load Estimate | 3.68 kW
High-Load Formula | P = 4 + (16 - 4) * ((x - 0.40) / 0.60)^2
Missing Data | Vendor RTC fan curve / field commissioning data
Future Update | Replace engineering fit with vendor curve when available
Software Read Sheet | Solver_Curve
Software Read Columns | load_ratio, power_kW