## YVAM Annual Estimate@25-17
YVAM1500--1300 KW@25C/17C Texas
|  |  |  | 100% |  | 90% |  | 80% |  | 70% |  | 65% |  | 60% |  | 55% |  | 50% |  | 45% |  | 40% |  | 35% |  | 30% |  | 25% |  | 20% |  | 15%
Bin Temp [F] | Average Ambient[F] | Average Ambient[C] | Total Operating Hours | kW | Annual kW | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh
110 - 115 | 112.5 | 44.7222 | 1 | 380.4 | 380.4 | 350.3 | 350.3 | 312 | 312 | 274.6 | 274.6 | 259.5 | 259.5 | 240.2 | 240.2 | 240.5 | 240.5 | 208.9 | 208.9 | 0 | 0 | 181.6 | 181.6 | 0 | 0 | 158.6 | 158.6 | 0 | 0 | 139 | 139 | 146.2 | 146.2
105 - 110 | 107.5 | 41.9444 | 24 | 341.1 | 8186.4 | 313.7 | 7528.8 | 277.6 | 6662.4 | 244.5 | 5868 | 237.5 | 5700 | 213.9 | 5133.6 | 215.5 | 5172 | 185.7 | 4456.8 | 0 | 0 | 161.4 | 3873.6 | 0 | 0 | 142.3 | 3415.2 | 0 | 0 | 123 | 2952 | 119.5 | 2868
100 - 105 | 102.5 | 39.1667 | 118 | 305.4 | 36037.2 | 280.4 | 33087.2 | 246.9 | 29134.2 | 216.7 | 25570.6 | 214.5 | 25311 | 190 | 22420 | 196.5 | 23187 | 164.7 | 19434.6 | 0 | 0 | 142.4 | 16803.2 | 0 | 0 | 123.2 | 14537.6 | 0 | 0 | 109.6 | 12932.8 | 103.9 | 12260.2
95 - 100 | 97.5 | 36.3889 | 283 | 273.2 | 77315.6 | 249.9 | 70721.7 | 220.7 | 62458.1 | 192.6 | 54505.8 | 189.5 | 53628.5 | 166.5 | 47119.5 | 179.5 | 50798.5 | 142.6 | 40355.8 | 0 | 0 | 121.2 | 34299.6 | 0 | 0 | 101.2 | 28639.6 | 0 | 0 | 93.83 | 26553.89 | 90.71 | 25670.93
90 - 95 | 92.5 | 33.6111 | 320 | 254 | 81280 | 231.4 | 74048 | 202.7 | 64864 | 175.5 | 56160 | 177.5 | 56800 | 151.4 | 48448 | 167.5 | 53600 | 129.3 | 41376 | 0 | 0 | 109.8 | 35136 | 0 | 0 | 91.72 | 29350.4 | 0 | 0 | 80.73 | 25833.6 | 81.25 | 26000
85 - 90 | 87.5 | 30.8333 | 652 | 226.3 | 147547.6 | 205 | 133660 | 178.7 | 116512.4 | 154.7 | 100864.4 | 160.5 | 104646 | 131.9 | 85998.8 | 148.5 | 96822 | 111.5 | 72698 | 0 | 0 | 93.49 | 60955.48 | 0 | 0 | 77.81 | 50732.12 | 0 | 0 | 67.13 | 43768.76 | 66.35 | 43260.2
80 - 85 | 82.5 | 28.0556 | 802 | 201.8 | 161843.6 | 181.4 | 145482.8 | 156.9 | 125833.8 | 134.3 | 107708.6 | 143.5 | 115087 | 113.7 | 91187.4 | 132.5 | 106265 | 95.33 | 76454.66 | 0 | 0 | 78.95 | 63317.9 | 0 | 0 | 64.53 | 51753.06 | 0 | 0 | 53.21 | 42674.42 | 52.03 | 41728.06
75 - 80 | 77.5 | 25.2778 | 977 | 178.2 | 174101.4 | 159.8 | 156124.6 | 137.3 | 134142.1 | 116.5 | 113820.5 | 129.5 | 126521.5 | 97.59 | 95345.43 | 113.5 | 110889.5 | 80.81 | 78951.37 | 0 | 0 | 65.32 | 63817.64 | 0 | 0 | 51.95 | 50755.15 | 0 | 0 | 41.02 | 40076.54 | 37.18 | 36324.86
70 - 75 | 72.5 | 22.5 | 606 | 164.1 | 99444.6 | 146.7 | 88900.2 | 125.3 | 75931.8 | 105.6 | 63993.6 | 122.5 | 74235 | 87.8 | 53206.8 | 106.5 | 64539 | 72.01 | 43638.06 | 0 | 0 | 58.07 | 35190.42 | 0 | 0 | 45.86 | 27791.16 | 0 | 0 | 35.7 | 21634.2 | 31.22 | 18919.32
65 - 70 | 67.5 | 19.7222 | 901 | 143.8 | 129563.8 | 127.8 | 115147.8 | 108.3 | 97578.3 | 90.35 | 81405.35 | 111.5 | 100461.5 | 74.36 | 66998.36 | 98.5 | 88748.5 | 60.12 | 54168.12 | 0 | 0 | 47.93 | 43184.93 | 0 | 0 | 36.98 | 33318.98 | 0 | 0 | 27.75 | 25002.75 | 23.9 | 21533.9
60 - 65 | 62.5 | 16.9444 | 750 | 124.9 | 93675 | 110.5 | 82875 | 92.69 | 69517.5 | 76.4 | 57300 | 102.5 | 76875 | 62.02 | 46515 | 90.5 | 67875 | 49.46 | 37095 | 0 | 0 | 38.54 | 28905 | 0 | 0 | 29.28 | 21960 | 0 | 0 | 21.09 | 15817.5 | 17.58 | 13185
55 - 60 | 57.5 | 14.1667 | 730 | 107.5 | 78475 | 94.44 | 68941.2 | 78.02 | 56954.6 | 63.48 | 46340.4 | 93.5 | 68255 | 50.72 | 37025.6 | 87.5 | 63875 | 39.44 | 28791.2 | 0 | 0 | 29.72 | 21695.6 | 0 | 0 | 21.61 | 15775.3 | 0 | 0 | 15.76 | 11504.8 | 14.06 | 10263.8
50 - 55 | 52.5 | 11.3889 | 653 | 92.56 | 60441.68 | 79.45 | 51880.85 | 64.74 | 42275.22 | 51.59 | 33688.27 | 91.5 | 59749.5 | 39.76 | 25963.28 | 87.5 | 57137.5 | 30.14 | 19681.42 | 0 | 0 | 22.24 | 14522.72 | 0 | 0 | 17.55 | 11460.15 | 0 | 0 | 14.8 | 9664.4 | 13.2 | 8619.6
45 - 50 | 47.5 | 8.6111 | 260 | 83.85 | 21801 | 71.03 | 18467.8 | 57.14 | 14856.4 | 44.17 | 11484.2 | 91.5 | 23790 | 34.62 | 9001.2 | 87.5 | 22750 | 26.67 | 6934.2 | 0 | 0 | 19.69 | 5119.4 | 0 | 0 | 16.82 | 4373.2 | 0 | 0 | 14.32 | 3723.2 | 13.06 | 3395.6
40 - 45 | 42.5 | 5.8333 | 409 | 73.2 | 29938.8 | 60.87 | 24895.83 | 48.31 | 19758.79 | 36.73 | 15022.57 | 91.5 | 37423.5 | 28.62 | 11705.58 | 87.5 | 35787.5 | 22.36 | 9145.24 | 0 | 0 | 18.07 | 7390.63 | 0 | 0 | 16.26 | 6650.34 | 0 | 0 | 14.06 | 5750.54 | 12.92 | 5284.28
35 - 40 | 37.5 | 3.0556 | 370 | 66.47 | 24593.9 | 54.89 | 20309.3 | 41.71 | 15432.7 | 32.1 | 11877 | 91.5 | 33855 | 25.37 | 9386.9 | 87.5 | 32375 | 20.45 | 7566.5 | 0 | 0 | 17.65 | 6530.5 | 0 | 0 | 16.33 | 6042.1 | 0 | 0 | 13.86 | 5128.2 | 12.94 | 4787.8
30 - 35 | 32.5 | 0.27778 | 367 | 62.43 | 22911.81 | 50.62 | 18577.54 | 37.73 | 13846.91 | 28.92 | 10613.64 | 91.5 | 33580.5 | 22.52 | 8264.84 | 87.5 | 32112.5 | 18.53 | 6800.51 | 0 | 0 | 16.79 | 6161.93 | 0 | 0 | 15.96 | 5857.32 | 0 | 0 | 14.28 | 5240.76 | 13.34 | 4895.78
25 - 30 | 27.5 | -2.5 | 234 | 59.26 | 13866.84 | 48.18 | 11274.12 | 35.88 | 8395.92 | 27.75 | 6493.5 | 91.5 | 21411 | 22.48 | 5260.32 | 87.5 | 20475 | 18.27 | 4275.18 | 0 | 0 | 16.58 | 3879.72 | 0 | 0 | 15.94 | 3729.96 | 0 | 0 | 13.81 | 3231.54 | 12.78 | 2990.52
20 - 25 | 22.5 | -5.2778 | 91 | 58.36 | 5310.76 | 47.34 | 4307.94 | 35.32 | 3214.12 | 27.42 | 2495.22 | 91.5 | 8326.5 | 22.53 | 2050.23 | 87.5 | 7962.5 | 18.42 | 1676.22 | 0 | 0 | 16.48 | 1499.68 | 0 | 0 | 15.83 | 1440.53 | 0 | 0 | 13.93 | 1267.63 | 12.77 | 1162.07
25 - 20 | 17.5 | -8.0556 | 140 | 57.6 | 8064 | 46.48 | 6507.2 | 37.08 | 5191.2 | 28.39 | 3974.6 | 0 | 0 | 22.97 | 3215.8 | 0 | 0 | 18.54 | 2595.6 | 0 | 0 | 16.46 | 2304.4 | 0 | 0 | 15.57 | 2179.8 | 0 | 0 | 13.93 | 1950.2 | 12.6763 | 1774.682
20 - 15 | 12.5 | -10.8333 | 56 | 57.57 | 3223.92 | 47.01 | 2632.56 | 36.16 | 2024.96 | 27.91 | 1562.96 |  |  | 22.63 | 1267.28 |  |  | 18.44 | 1032.64 |  |  | 16.4 | 918.4 |  |  | 15.62 | 874.72 |  |  | 14.26 | 798.56 | 12.9766 | 726.6896
15 - 10 | 7.5 | -13.6111 | 10 | 56.91 | 569.1 | 46.35 | 463.5 | 35.36 | 353.6 | 27.75 | 277.5 |  |  | 22.87 | 228.7 |  |  | 18.43 | 184.3 |  |  | 16.32 | 163.2 |  |  | 15.59 | 155.9 |  |  | 14.12 | 141.2 | 12.8492 | 128.492
10 - 05 | 2.5 | -16.3889 | 6 | 57.16 | 342.96 | 45.77 | 274.62 | 36.8 | 220.8 | 28.46 | 170.76 |  |  | 23.07 | 138.42 |  |  | 18.19 | 109.14 |  |  | 16.39 | 98.34 |  |  | 15.53 | 93.18 |  |  | 14.2 | 85.2 | 12.922 | 77.532
|  |  | 8760 |  | 1278915.37 |  | 1136458.86 |  | 965471.82 |  | 811472.07 |  | 1025916 |  | 676121.24 |  | 940612 |  | 557629.46 |  | 0 |  | 455949.89 |  | 0 |  | 371044.37 |  | 0 |  | 305871.69 |  | 286003.5156

## YVAM chiller load reference
Input power
100 | 46.1 | 1300 | 396.6 | 3.278 | 529.5 | 100 | 46.1 | 1300 | 415.4 | 3.129 | 560.5 | 100 | 46.1 | 1300 | 415.4 | 3.129 | 560.5 | 100 | 46.1 | 1300 | 415.4 | 3.129 | 560.5 | 100 | 46.1 | 1300 | 415.4 | 3.129 | 560.5 | 100 | 46.1 | 1300 | 415.4 | 3.129 | 560.5 | 100 | 46.1 | 1300 | 415.4 | 3.129 | 560.5 | 100 | 46.1 | 1300 | 415.4 | 3.129 | 560.5 | 100 | 46.1 | 1300 | 415.4 | 3.129 | 560.5 | 100 | 46.1 | 1300 | 415.4 | 3.129 | 560.5
100 | 45 | 1300 | 380.4 | 3.418 | 508.5 | 90 | 45 | 1170 | 350.3 | 3.34 | 475.5 | 80 | 45 | 1040 | 312 | 3.334 | 430.5 | 70 | 45 | 910.2 | 274.6 | 3.315 | 379.5 | 60 | 45 | 780 | 240.2 | 3.247 | 342.5 | 50 | 45 | 649.9 | 208.9 | 3.112 | 309.5 | 40 | 45 | 520.1 | 181.6 | 2.864 | 281.5 | 30 | 45 | 390 | 158.6 | 2.459 | 259.5 | 20 | 45 | 260 | 139 | 1.87 | 238.5 | 15 | 45 | 195 | 146.2 | 1.334 | 240.5
100 | 42 | 1300 | 341.1 | 3.812 | 460.5 | 90 | 42 | 1170 | 313.7 | 3.729 | 429.5 | 80 | 42 | 1040 | 277.6 | 3.747 | 380.5 | 70 | 42 | 910.2 | 244.5 | 3.721 | 345.5 | 60 | 42 | 780 | 213.9 | 3.647 | 314.5 | 50 | 42 | 649.9 | 185.7 | 3.5 | 283.5 | 40 | 42 | 520.1 | 161.4 | 3.221 | 258.5 | 30 | 42 | 390 | 142.3 | 2.741 | 237.5 | 20 | 42 | 260 | 123 | 2.115 | 218.5 | 15 | 42 | 195 | 119.5 | 1.632 | 215.5
100 | 39 | 1300 | 305.4 | 4.257 | 417.5 | 90 | 39 | 1170 | 280.4 | 4.172 | 388.5 | 80 | 39 | 1040 | 246.9 | 4.212 | 345.5 | 70 | 39 | 910.2 | 216.7 | 4.199 | 315.5 | 60 | 39 | 780 | 190 | 4.105 | 285.5 | 50 | 39 | 649.9 | 164.7 | 3.948 | 260.5 | 40 | 39 | 520.1 | 142.4 | 3.651 | 236.5 | 30 | 39 | 390 | 123.2 | 3.166 | 214.5 | 20 | 39 | 260 | 109.6 | 2.372 | 201.5 | 15 | 39 | 195 | 103.9 | 1.876 | 196.5
100 | 36 | 1300 | 273.2 | 4.759 | 373.5 | 90 | 36 | 1170 | 249.9 | 4.682 | 351.5 | 80 | 36 | 1040 | 220.7 | 4.712 | 313.5 | 70 | 36 | 910.2 | 192.6 | 4.724 | 284.5 | 60 | 36 | 780 | 166.5 | 4.686 | 253.5 | 50 | 36 | 649.9 | 142.6 | 4.56 | 230.5 | 40 | 36 | 520.1 | 121.2 | 4.291 | 211.5 | 30 | 36 | 390 | 101.2 | 3.855 | 189.5 | 20 | 36 | 260 | 93.83 | 2.771 | 181.5 | 15 | 36 | 195 | 90.71 | 2.15 | 179.5
100 | 34 | 1300 | 254 | 5.118 | 350.5 | 90 | 34 | 1170 | 231.4 | 5.056 | 325.5 | 80 | 34 | 1040 | 202.7 | 5.13 | 295.5 | 70 | 34 | 910.2 | 175.5 | 5.184 | 265.5 | 60 | 34 | 780 | 151.4 | 5.153 | 241.5 | 50 | 34 | 649.9 | 129.3 | 5.026 | 217.5 | 40 | 34 | 520.1 | 109.8 | 4.738 | 196.5 | 30 | 34 | 390 | 91.72 | 4.252 | 177.5 | 20 | 34 | 260 | 80.73 | 3.221 | 163.5 | 15 | 34 | 195 | 81.25 | 2.401 | 167.5
100 | 31 | 1300 | 226.3 | 5.745 | 320.5 | 90 | 31 | 1170 | 205 | 5.708 | 296.5 | 80 | 31 | 1040 | 178.7 | 5.821 | 265.5 | 70 | 31 | 910.2 | 154.7 | 5.883 | 240.5 | 60 | 31 | 780 | 131.9 | 5.915 | 216.5 | 50 | 31 | 649.9 | 111.5 | 5.832 | 196.5 | 40 | 31 | 520.1 | 93.49 | 5.562 | 176.5 | 30 | 31 | 390 | 77.81 | 5.012 | 160.5 | 20 | 31 | 260 | 67.13 | 3.873 | 149.5 | 15 | 31 | 195 | 66.35 | 2.938 | 148.5
100 | 28 | 1300 | 201.8 | 6.441 | 290.5 | 90 | 28 | 1170 | 181.4 | 6.45 | 267.5 | 80 | 28 | 1040 | 156.9 | 6.63 | 242.5 | 70 | 28 | 910.2 | 134.3 | 6.775 | 218.5 | 60 | 28 | 780 | 113.7 | 6.86 | 195.5 | 50 | 28 | 649.9 | 95.33 | 6.819 | 176.5 | 40 | 28 | 520.1 | 78.95 | 6.586 | 158.5 | 30 | 28 | 390 | 64.53 | 6.044 | 143.5 | 20 | 28 | 260 | 53.21 | 4.887 | 131.5 | 15 | 28 | 195 | 52.03 | 3.748 | 132.5
100 | 25 | 1300 | 178.2 | 7.295 | 265.5 | 90 | 25 | 1170 | 159.8 | 7.323 | 244.5 | 80 | 25 | 1040 | 137.3 | 7.576 | 220.5 | 70 | 25 | 910.2 | 116.5 | 7.809 | 196.5 | 60 | 25 | 780 | 97.59 | 7.993 | 177.5 | 50 | 25 | 649.9 | 80.81 | 8.044 | 158.5 | 40 | 25 | 520.1 | 65.32 | 7.961 | 143.5 | 30 | 25 | 390 | 51.95 | 7.509 | 129.5 | 20 | 25 | 260 | 41.02 | 6.338 | 118.5 | 15 | 25 | 195 | 37.18 | 5.245 | 113.5
100 | 23 | 1300 | 164.1 | 7.923 | 247.5 | 90 | 23 | 1170 | 146.7 | 7.977 | 227.5 | 80 | 23 | 1040 | 125.3 | 8.301 | 205.5 | 70 | 23 | 910.2 | 105.6 | 8.618 | 185.5 | 60 | 23 | 780 | 87.8 | 8.884 | 164.5 | 50 | 23 | 649.9 | 72.01 | 9.027 | 148.5 | 40 | 23 | 520.1 | 58.07 | 8.956 | 134.5 | 30 | 23 | 390 | 45.86 | 8.505 | 122.5 | 20 | 23 | 260 | 35.7 | 7.283 | 111.5 | 15 | 23 | 195 | 31.22 | 6.247 | 106.5
100 | 20 | 1300 | 143.8 | 9.041 | 223.5 | 90 | 20 | 1170 | 127.8 | 9.154 | 206.5 | 80 | 20 | 1040 | 108.3 | 9.607 | 186.5 | 70 | 20 | 910.2 | 90.35 | 10.07 | 166.5 | 60 | 20 | 780 | 74.36 | 10.49 | 149.5 | 50 | 20 | 649.9 | 60.12 | 10.81 | 135.5 | 40 | 20 | 520.1 | 47.93 | 10.85 | 122.5 | 30 | 20 | 390 | 36.98 | 10.55 | 111.5 | 20 | 20 | 260 | 27.75 | 9.371 | 101.5 | 15 | 20 | 195 | 23.9 | 8.16 | 98.5
100 | 17 | 1300 | 124.9 | 10.41 | 201.5 | 90 | 17 | 1170 | 110.5 | 10.59 | 185.5 | 80 | 17 | 1040 | 92.69 | 11.22 | 166.5 | 70 | 17 | 910.2 | 76.4 | 11.91 | 150.5 | 60 | 17 | 780 | 62.02 | 12.58 | 135.5 | 50 | 17 | 649.9 | 49.46 | 13.14 | 122.5 | 40 | 17 | 520.1 | 38.54 | 13.49 | 111.5 | 30 | 17 | 390 | 29.28 | 13.32 | 102.5 | 20 | 17 | 260 | 21.09 | 12.33 | 93.5 | 15 | 17 | 195 | 17.58 | 11.09 | 90.5
100 | 14 | 1300 | 107.5 | 12.09 | 182.5 | 90 | 14 | 1170 | 94.44 | 12.39 | 168.5 | 80 | 14 | 1040 | 78.02 | 13.33 | 150.5 | 70 | 14 | 910.2 | 63.48 | 14.34 | 135.5 | 60 | 14 | 780 | 50.72 | 15.38 | 122.5 | 50 | 14 | 649.9 | 39.44 | 16.48 | 109.5 | 40 | 14 | 520.1 | 29.72 | 17.5 | 100.5 | 30 | 14 | 390 | 21.61 | 18.05 | 93.5 | 20 | 14 | 260 | 15.76 | 16.5 | 89.5 | 15 | 14 | 195 | 14.06 | 13.87 | 87.5
100 | 11 | 1300 | 92.56 | 14.05 | 168.5 | 90 | 11 | 1170 | 79.45 | 14.73 | 150.5 | 80 | 11 | 1040 | 64.74 | 16.07 | 136.5 | 70 | 11 | 910.2 | 51.59 | 17.64 | 119.5 | 60 | 11 | 780 | 39.76 | 19.63 | 108.5 | 50 | 11 | 649.9 | 30.14 | 21.56 | 99.5 | 40 | 11 | 520.1 | 22.24 | 23.38 | 93.5 | 30 | 11 | 390 | 17.55 | 22.23 | 91.5 | 20 | 11 | 260 | 14.8 | 17.57 | 89.5 | 15 | 11 | 195 | 13.2 | 14.77 | 87.5
100 | 9 | 1300 | 83.85 | 15.51 | 156.5 | 90 | 9 | 1170 | 71.03 | 16.47 | 144.5 | 80 | 9 | 1040 | 57.14 | 18.2 | 128.5 | 70 | 9 | 910.2 | 44.17 | 20.6 | 115.5 | 60 | 9 | 780 | 34.62 | 22.53 | 107.5 | 50 | 9 | 649.9 | 26.67 | 24.37 | 100.5 | 40 | 9 | 520.1 | 19.69 | 26.4 | 93.5 | 30 | 9 | 390 | 16.82 | 23.18 | 91.5 | 20 | 9 | 260 | 14.32 | 18.15 | 88.5 | 15 | 9 | 195 | 13.06 | 14.93 | 87.5
100 | 6 | 1300 | 73.2 | 17.76 | 152.5 | 90 | 6 | 1170 | 60.87 | 19.22 | 135.5 | 80 | 6 | 1040 | 48.31 | 21.52 | 122.5 | 70 | 6 | 910.2 | 36.73 | 24.77 | 110.5 | 60 | 6 | 780 | 28.62 | 27.26 | 102.5 | 50 | 6 | 649.9 | 22.36 | 29.07 | 96.5 | 40 | 6 | 520.1 | 18.07 | 28.78 | 92.5 | 30 | 6 | 390 | 16.26 | 23.99 | 91.5 | 20 | 6 | 260 | 14.06 | 18.49 | 88.5 | 15 | 6 | 195 | 12.92 | 15.09 | 87.5
100 | 3 | 1300 | 66.47 | 19.56 | 148.5 | 90 | 3 | 1170 | 54.89 | 21.32 | 133.5 | 80 | 3 | 1040 | 41.71 | 24.94 | 117.5 | 70 | 3 | 910.2 | 32.1 | 28.34 | 107.5 | 60 | 3 | 780 | 25.37 | 30.74 | 100.5 | 50 | 3 | 649.9 | 20.45 | 31.77 | 95.5 | 40 | 3 | 520.1 | 17.65 | 29.46 | 92.5 | 30 | 3 | 390 | 16.33 | 23.88 | 91.5 | 20 | 3 | 260 | 13.86 | 18.76 | 88.5 | 15 | 3 | 195 | 12.94 | 15.07 | 87.5
100 | 0 | 1300 | 62.43 | 20.82 | 144.5 | 90 | 0 | 1170 | 50.62 | 23.11 | 130.5 | 80 | 0 | 1040 | 37.73 | 27.56 | 114.5 | 70 | 0 | 910.2 | 28.92 | 31.46 | 104.5 | 60 | 0 | 780 | 22.52 | 34.62 | 97.5 | 50 | 0 | 649.9 | 18.53 | 35.1 | 93.5 | 40 | 0 | 520.1 | 16.79 | 30.96 | 91.5 | 30 | 0 | 390 | 15.96 | 24.42 | 91.5 | 20 | 0 | 260 | 14.28 | 18.21 | 89.5 | 15 | 0 | 195 | 13.34 | 14.61 | 87.5
100 | -3 | 1300 | 59.26 | 21.94 | 142.5 | 90 | -3 | 1170 | 48.18 | 24.29 | 128.5 | 80 | -3 | 1040 | 35.88 | 28.99 | 114.5 | 70 | -3 | 910.2 | 27.75 | 32.81 | 104.5 | 60 | -3 | 780 | 22.48 | 34.68 | 98.5 | 50 | -3 | 649.9 | 18.27 | 35.59 | 93.5 | 40 | -3 | 520.1 | 16.58 | 31.35 | 91.5 | 30 | -3 | 390 | 15.94 | 24.47 | 91.5 | 20 | -3 | 260 | 13.81 | 18.83 | 88.5 | 15 | -3 | 195 | 12.78 | 15.25 | 87.5
100 | -5 | 1300 | 58.36 | 22.27 | 142.5 | 90 | -5 | 1170 | 47.34 | 24.72 | 128.5 | 80 | -5 | 1040 | 35.32 | 29.46 | 114.5 | 70 | -5 | 910.2 | 27.42 | 33.18 | 104.5 | 60 | -5 | 780 | 22.53 | 34.62 | 98.5 | 50 | -5 | 649.9 | 18.42 | 35.29 | 93.5 | 40 | -5 | 520.1 | 16.48 | 31.57 | 91.5 | 30 | -5 | 390 | 15.83 | 24.63 | 91.5 | 20 | -5 | 260 | 13.93 | 18.67 | 88.5 | 15 | -5 | 195 | 12.77 | 15.27 | 87.5

## YVAM Annual Estimate @33-25
YVAM1500--1300 KW@33C/25C Texas
|  |  |  | 100% |  | 90% |  | 80% |  | 70% |  | 65% |  | 60% |  | 50% |  | 40% |  | 30% |  | 25% |  | 20% |  | 15%
Bin Temp [F] | Average Ambient[F] | Average Ambient[C] | Total Operating Hours | kW | Annual kW | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh | kW | Annual kWh
110 - 115 | 112.5 | 44.7222 | 1 | 289.4 | 289.4 | 259.1 | 259.1 | 230.1 | 230.1 | 202.9 | 202.9 | 203.5 | 203.5 | 177 | 177 | 153 | 153 | 132 | 132 | 117.9 | 117.9 | 0 | 0 | 114 | 114 | 111.7 | 111.7
105 - 110 | 107.5 | 41.9444 | 24 | 256.9 | 6165.6 | 226.8 | 5443.2 | 200.8 | 4819.2 | 176.5 | 4236 | 185.5 | 4452 | 153.8 | 3691.2 | 133.3 | 3199.2 | 114.2 | 2740.8 | 98.73 | 2369.52 | 0 | 0 | 93.41 | 2241.84 | 95.76 | 2298.24
100 - 105 | 102.5 | 39.1667 | 118 | 226.4 | 26715.2 | 200.4 | 23647.2 | 175.8 | 20744.4 | 153.2 | 18077.6 | 165.5 | 19529 | 132.4 | 15623.2 | 113.6 | 13404.8 | 97.23 | 11473.14 | 83.01 | 9795.18 | 0 | 0 | 76.03 | 8971.54 | 76.9 | 9074.2
95 - 100 | 97.5 | 36.3889 | 283 | 199.4 | 56430.2 | 175.1 | 49553.3 | 152.7 | 43214.1 | 132 | 37356 | 145.5 | 41176.5 | 113.4 | 32092.2 | 96.31 | 27255.73 | 80.62 | 22815.46 | 67.65 | 19144.95 | 0 | 0 | 58.84 | 16651.72 | 60.63 | 17158.29
90 - 95 | 92.5 | 33.6111 | 320 | 182.9 | 58528 | 159.9 | 51168 | 138.8 | 44416 | 119.3 | 38176 | 135.5 | 43360 | 101.7 | 32544 | 85.43 | 27337.6 | 70.19 | 22460.8 | 57.46 | 18387.2 | 0 | 0 | 48.49 | 15516.8 | 47.09 | 15068.8
85 - 90 | 87.5 | 30.8333 | 652 | 159.9 | 104254.8 | 138.8 | 90497.6 | 119.6 | 77979.2 | 101.7 | 66308.4 | 124.5 | 81174 | 85.76 | 55915.52 | 71.46 | 46591.92 | 58.39 | 38070.28 | 47.15 | 30741.8 | 0 | 0 | 37.56 | 24489.12 | 33.87 | 22083.24
80 - 85 | 82.5 | 28.0556 | 802 | 138.7 | 111237.4 | 119.3 | 95678.6 | 102 | 81804 | 86.1 | 69052.2 | 111.5 | 89423 | 71.63 | 57447.26 | 59.02 | 47334.04 | 47.59 | 38167.18 | 37.39 | 29986.78 | 0 | 0 | 28.52 | 22873.04 | 24.84 | 19921.68
75 - 80 | 77.5 | 25.2778 | 977 | 119 | 116263 | 101.6 | 99263.2 | 85.89 | 83914.53 | 71.7 | 70050.9 | 100.5 | 98188.5 | 58.88 | 57525.76 | 47.63 | 46534.51 | 37.57 | 36705.89 | 28.9 | 28235.3 | 0 | 0 | 21.11 | 20624.47 | 17.74 | 17331.98
70 - 75 | 72.5 | 22.5 | 606 | 106.7 | 64660.2 | 90.23 | 54679.38 | 75.89 | 45989.34 | 62.73 | 38014.38 | 95.5 | 57873 | 50.93 | 30863.58 | 40.45 | 24512.7 | 31.18 | 18895.08 | 23.21 | 14065.26 | 0 | 0 | 17.14 | 10386.84 | 14.87 | 9011.22
65 - 70 | 67.5 | 19.7222 | 901 | 89.2 | 80369.2 | 74.85 | 67439.85 | 61.84 | 55717.84 | 49.83 | 44896.83 | 92.5 | 83342.5 | 39.45 | 35544.45 | 30.34 | 27336.34 | 23.17 | 20876.17 | 18.56 | 16722.56 | 0 | 0 | 15.32 | 13803.32 | 13.69 | 12334.69
60 - 65 | 62.5 | 16.9444 | 750 | 74.07 | 55552.5 | 60.49 | 45367.5 | 48.05 | 36037.5 | 38.15 | 28612.5 | 92.5 | 69375 | 29.86 | 22395 | 23.88 | 17910 | 19.96 | 14970 | 17.41 | 13057.5 | 0 | 0 | 14.66 | 10995 | 13.44 | 10080
55 - 60 | 57.5 | 14.1667 | 730 | 61.65 | 45004.5 | 48.81 | 35631.3 | 38.97 | 28448.1 | 31.2 | 22776 | 92.5 | 67525 | 24.65 | 17994.5 | 20.93 | 15278.9 | 18.69 | 13643.7 | 16.94 | 12366.2 | 0 | 0 | 14.45 | 10548.5 | 13.31 | 9716.3
50 - 55 | 52.5 | 11.3889 | 653 | 53.13 | 34693.89 | 41.62 | 27177.86 | 33.68 | 21993.04 | 27.25 | 17794.25 | 91.5 | 59749.5 | 22.18 | 14483.54 | 19.74 | 12890.22 | 18.41 | 12021.73 | 16.63 | 10859.39 | 0 | 0 | 14.32 | 9350.96 | 13.25 | 8652.25
45 - 50 | 47.5 | 8.6111 | 260 | 49.36 | 12833.6 | 38.62 | 10041.2 | 31.21 | 8114.6 | 25.28 | 6572.8 | 91.5 | 23790 | 21.16 | 5501.6 | 19.18 | 4986.8 | 18.09 | 4703.4 | 16.48 | 4284.8 | 0 | 0 | 14.81 | 3850.6 | 13.19 | 3429.4
40 - 45 | 42.5 | 5.8333 | 409 | 45.21 | 18490.89 | 35.86 | 14666.74 | 29.14 | 11918.26 | 23.41 | 9574.69 | 91.5 | 37423.5 | 20.53 | 8396.77 | 19.07 | 7799.63 | 17.95 | 7341.55 | 16.36 | 6691.24 | 0 | 0 | 14.88 | 6085.92 | 13.73 | 5615.57
35 - 40 | 37.5 | 3.0556 | 370 | 43.48 | 16087.6 | 34.6 | 12802 | 28.83 | 10667.1 | 23.36 | 8643.2 | 91.5 | 33855 | 20.21 | 7477.7 | 18.8 | 6956 | 17.97 | 6648.9 | 16.33 | 6042.1 | 0 | 0 | 14.56 | 5387.2 | 13.14 | 4861.8
30 - 35 | 32.5 | 0.27778 | 367 | 42.56 | 15619.52 | 33.9 | 12441.3 | 27.78 | 10195.26 | 24.29 | 8914.43 | 91.5 | 33580.5 | 20.02 | 7347.34 | 18.64 | 6840.88 | 17.74 | 6510.58 | 16.49 | 6051.83 | 0 | 0 | 14.35 | 5266.45 | 17.01 | 6242.67
25 - 30 | 27.5 | -2.5 | 234 | 41.86 | 9795.24 | 33.55 | 7850.7 | 29.31 | 6858.54 | 22.91 | 5360.94 | 91.5 | 21411 | 19.86 | 4647.24 | 18.54 | 4338.36 | 17.67 | 4134.78 | 16.32 | 3818.88 | 0 | 0 | 14.8 | 3463.2 | 0 | 0
20 - 25 | 22.5 | -5.2778 | 91 | 44.35 | 4035.85 | 34.27 | 3118.57 | 28.1 | 2557.1 | 23.57 | 2144.87 | 91.5 | 8326.5 | 19.82 | 1803.62 | 18.49 | 1682.59 | 17.64 | 1605.24 | 16.35 | 1487.85 | 0 | 0 | 14.37 | 1307.67 | 0 | 0
25 - 20 | 17.5 | -8.0556 | 140 | 42.57 | 5959.8 | 33.77 | 4727.8 | 28.39 | 3974.6 | 23.28 | 3259.2 | 0 | 0 | 19.8 | 2772 | 18.41 | 2577.4 | 17.66 | 2472.4 | 16.65 | 2331 | 0 | 0 | 0 | 0 | 0 | 0
20 - 15 | 12.5 | -10.8333 | 56 | 41.69 | 2334.64 | 34.4 | 1926.4 | 28.46 | 1593.76 | 23.86 | 1336.16 |  |  | 19.83 | 1110.48 | 18.39 | 1029.84 | 17.7 | 991.2 | 16.54 | 926.24 |  |  | 0 | 0 | 0 | 0
15 - 10 | 7.5 | -13.6111 | 10 | 42.66 | 426.6 | 34.48 | 344.8 | 27.76 | 277.6 | 22.83 | 228.3 |  |  | 19.8 | 198 | 18.36 | 183.6 | 17.62 | 176.2 | 16.55 | 165.5 |  |  | 0 | 0 | 0 | 0
10 - 05 | 2.5 | -16.3889 | 6 | 42.09 | 252.54 | 33.63 | 201.78 | 28.19 | 169.14 | 22.95 | 137.7 |  |  | 19.76 | 118.56 | 18.35 | 110.1 | 17.62 | 105.72 | 16.43 | 98.58 |  |  | 0 | 0 | 0 | 0
|  |  | 8760 |  | 846000.17 |  | 713927.38 |  | 601633.31 |  | 501726.25 |  | 873758 |  | 415670.52 |  | 346244.16 |  | 287662.2 |  | 236557.24 |  | 0 |  | 191928.19 |  | 172992.03

## YVAM chiller load reference
Input power
100 | 46.1 | 1300 | 305 | 4.263 | 415.5 | 100 | 46.1 | 1300 | 305 | 4.263 | 415.5 | 100 | 46.1 | 1300 | 305 | 4.263 | 415.5 | 100 | 46.1 | 1300 | 305 | 4.263 | 415.5 | 100 | 46.1 | 1300 | 305 | 4.263 | 415.5 | 100 | 46.1 | 1300 | 305 | 4.263 | 415.5 | 100 | 46.1 | 1300 | 305 | 4.263 | 415.5 | 100 | 46.1 | 1300 | 305 | 4.263 | 415.5 | 100 | 46.1 | 1300 | 305 | 4.263 | 415.5 | 100 | 46.1 | 1300 | 305 | 4.263 | 415.5
100 | 45 | 1300 | 289.4 | 4.492 | 396.5 | 90 | 45 | 1170 | 259.1 | 4.515 | 358.5 | 80 | 45 | 1040 | 230.1 | 4.519 | 322.5 | 70 | 45 | 910.2 | 202.9 | 4.486 | 300.5 | 60 | 45 | 780 | 177 | 4.407 | 268.5 | 50 | 45 | 649.9 | 153 | 4.249 | 246.5 | 40 | 45 | 520.1 | 132 | 3.939 | 223.5 | 30 | 45 | 390 | 117.9 | 3.309 | 203.5 | 20 | 45 | 260 | 114 | 2.282 | 206.5 | 15 | 45 | 195 | 111.7 | 1.746 | 205.5
100 | 42 | 1300 | 256.9 | 5.061 | 357.5 | 90 | 42 | 1170 | 226.8 | 5.159 | 319.5 | 80 | 42 | 1040 | 200.8 | 5.18 | 292.5 | 70 | 42 | 910.2 | 176.5 | 5.155 | 268.5 | 60 | 42 | 780 | 153.8 | 5.073 | 242.5 | 50 | 42 | 649.9 | 133.3 | 4.876 | 220.5 | 40 | 42 | 520.1 | 114.2 | 4.552 | 201.5 | 30 | 42 | 390 | 98.73 | 3.95 | 185.5 | 20 | 42 | 260 | 93.41 | 2.785 | 179.5 | 15 | 42 | 195 | 95.76 | 2.036 | 186.5
100 | 39 | 1300 | 226.4 | 5.742 | 320.5 | 90 | 39 | 1170 | 200.4 | 5.839 | 287.5 | 80 | 39 | 1040 | 175.8 | 5.918 | 262.5 | 70 | 39 | 910.2 | 153.2 | 5.942 | 240.5 | 60 | 39 | 780 | 132.4 | 5.891 | 217.5 | 50 | 39 | 649.9 | 113.6 | 5.721 | 197.5 | 40 | 39 | 520.1 | 97.23 | 5.348 | 180.5 | 30 | 39 | 390 | 83.01 | 4.698 | 165.5 | 20 | 39 | 260 | 76.03 | 3.421 | 159.5 | 15 | 39 | 195 | 76.9 | 2.536 | 162.5
100 | 36 | 1300 | 199.4 | 6.52 | 287.5 | 90 | 36 | 1170 | 175.1 | 6.682 | 261.5 | 80 | 36 | 1040 | 152.7 | 6.809 | 235.5 | 70 | 36 | 910.2 | 132 | 6.892 | 214.5 | 60 | 36 | 780 | 113.4 | 6.876 | 195.5 | 50 | 36 | 649.9 | 96.31 | 6.749 | 177.5 | 40 | 36 | 520.1 | 80.62 | 6.45 | 160.5 | 30 | 36 | 390 | 67.65 | 5.766 | 145.5 | 20 | 36 | 260 | 58.84 | 4.419 | 137.5 | 15 | 36 | 195 | 60.63 | 3.218 | 141.5
100 | 34 | 1300 | 182.9 | 7.106 | 266.5 | 90 | 34 | 1170 | 159.9 | 7.318 | 243.5 | 80 | 34 | 1040 | 138.8 | 7.494 | 221.5 | 70 | 34 | 910.2 | 119.3 | 7.629 | 201.5 | 60 | 34 | 780 | 101.7 | 7.672 | 181.5 | 50 | 34 | 649.9 | 85.43 | 7.609 | 164.5 | 40 | 34 | 520.1 | 70.19 | 7.409 | 149.5 | 30 | 34 | 390 | 57.46 | 6.787 | 135.5 | 20 | 34 | 260 | 48.49 | 5.362 | 125.5 | 15 | 34 | 195 | 47.09 | 4.142 | 125.5
100 | 31 | 1300 | 159.9 | 8.128 | 241.5 | 90 | 31 | 1170 | 138.8 | 8.43 | 216.5 | 80 | 31 | 1040 | 119.6 | 8.695 | 197.5 | 70 | 31 | 910.2 | 101.7 | 8.947 | 179.5 | 60 | 31 | 780 | 85.76 | 9.095 | 163.5 | 50 | 31 | 649.9 | 71.46 | 9.095 | 149.5 | 40 | 31 | 520.1 | 58.39 | 8.906 | 135.5 | 30 | 31 | 390 | 47.15 | 8.273 | 124.5 | 20 | 31 | 260 | 37.56 | 6.923 | 113.5 | 15 | 31 | 195 | 33.87 | 5.757 | 109.5
100 | 28 | 1300 | 138.7 | 9.374 | 216.5 | 90 | 28 | 1170 | 119.3 | 9.81 | 196.5 | 80 | 28 | 1040 | 102 | 10.19 | 178.5 | 70 | 28 | 910.2 | 86.1 | 10.57 | 161.5 | 60 | 28 | 780 | 71.63 | 10.89 | 147.5 | 50 | 28 | 649.9 | 59.02 | 11.01 | 134.5 | 40 | 28 | 520.1 | 47.59 | 10.93 | 122.5 | 30 | 28 | 390 | 37.39 | 10.43 | 111.5 | 20 | 28 | 260 | 28.52 | 9.116 | 103.5 | 15 | 28 | 195 | 24.84 | 7.852 | 99.5
100 | 25 | 1300 | 119 | 10.92 | 194.5 | 90 | 25 | 1170 | 101.6 | 11.52 | 176.5 | 80 | 25 | 1040 | 85.89 | 12.11 | 159.5 | 70 | 25 | 910.2 | 71.7 | 12.69 | 144.5 | 60 | 25 | 780 | 58.88 | 13.25 | 131.5 | 50 | 25 | 649.9 | 47.63 | 13.65 | 120.5 | 40 | 25 | 520.1 | 37.57 | 13.84 | 109.5 | 30 | 25 | 390 | 28.9 | 13.5 | 100.5 | 20 | 25 | 260 | 21.11 | 12.32 | 93.5 | 15 | 25 | 195 | 17.74 | 10.99 | 90.5
100 | 23 | 1300 | 106.7 | 12.19 | 178.5 | 90 | 23 | 1170 | 90.23 | 12.97 | 161.5 | 80 | 23 | 1040 | 75.89 | 13.71 | 147.5 | 70 | 23 | 910.2 | 62.73 | 14.51 | 133.5 | 60 | 23 | 780 | 50.93 | 15.32 | 122.5 | 50 | 23 | 649.9 | 40.45 | 16.07 | 112.5 | 40 | 23 | 520.1 | 31.18 | 16.68 | 101.5 | 30 | 23 | 390 | 23.21 | 16.8 | 95.5 | 20 | 23 | 260 | 17.14 | 15.17 | 90.5 | 15 | 23 | 195 | 14.87 | 13.11 | 88.5
100 | 20 | 1300 | 89.2 | 14.58 | 159.5 | 90 | 20 | 1170 | 74.85 | 15.63 | 143.5 | 80 | 20 | 1040 | 61.84 | 16.82 | 129.5 | 70 | 20 | 910.2 | 49.83 | 18.26 | 117.5 | 60 | 20 | 780 | 39.45 | 19.77 | 108.5 | 50 | 20 | 649.9 | 30.34 | 21.42 | 99.5 | 40 | 20 | 520.1 | 23.17 | 22.44 | 94.5 | 30 | 20 | 390 | 18.56 | 21.01 | 92.5 | 20 | 20 | 260 | 15.32 | 16.97 | 89.5 | 15 | 20 | 195 | 13.69 | 14.25 | 87.5
100 | 17 | 1300 | 74.07 | 17.55 | 145.5 | 90 | 17 | 1170 | 60.49 | 19.35 | 127.5 | 80 | 17 | 1040 | 48.05 | 21.64 | 115.5 | 70 | 17 | 910.2 | 38.15 | 23.86 | 106.5 | 60 | 17 | 780 | 29.86 | 26.13 | 100.5 | 50 | 17 | 649.9 | 23.88 | 27.22 | 96.5 | 40 | 17 | 520.1 | 19.96 | 26.05 | 93.5 | 30 | 17 | 390 | 17.41 | 22.4 | 92.5 | 20 | 17 | 260 | 14.66 | 17.74 | 89.5 | 15 | 17 | 195 | 13.44 | 14.52 | 87.5
100 | 14 | 1300 | 61.65 | 21.09 | 133.5 | 90 | 14 | 1170 | 48.81 | 23.97 | 120.5 | 80 | 14 | 1040 | 38.97 | 26.68 | 111.5 | 70 | 14 | 910.2 | 31.2 | 29.16 | 103.5 | 60 | 14 | 780 | 24.65 | 31.63 | 98.5 | 50 | 14 | 649.9 | 20.93 | 31.07 | 94.5 | 40 | 14 | 520.1 | 18.69 | 27.82 | 93.5 | 30 | 14 | 390 | 16.94 | 23.03 | 92.5 | 20 | 14 | 260 | 14.45 | 17.99 | 89.5 | 15 | 14 | 195 | 13.31 | 14.65 | 87.5
100 | 11 | 1300 | 53.13 | 24.47 | 128.5 | 90 | 11 | 1170 | 41.62 | 28.11 | 116.5 | 80 | 11 | 1040 | 33.68 | 30.88 | 108.5 | 70 | 11 | 910.2 | 27.25 | 33.4 | 101.5 | 60 | 11 | 780 | 22.18 | 35.17 | 96.5 | 50 | 11 | 649.9 | 19.74 | 32.93 | 94.5 | 40 | 11 | 520.1 | 18.41 | 28.25 | 93.5 | 30 | 11 | 390 | 16.63 | 23.46 | 91.5 | 20 | 11 | 260 | 14.32 | 18.16 | 89.5 | 15 | 11 | 195 | 13.25 | 14.72 | 87.5
100 | 9 | 1300 | 49.36 | 26.34 | 126.5 | 90 | 9 | 1170 | 38.62 | 30.29 | 114.5 | 80 | 9 | 1040 | 31.21 | 33.34 | 106.5 | 70 | 9 | 910.2 | 25.28 | 35.99 | 100.5 | 60 | 9 | 780 | 21.16 | 36.86 | 95.5 | 50 | 9 | 649.9 | 19.18 | 33.88 | 94.5 | 40 | 9 | 520.1 | 18.09 | 28.76 | 93.5 | 30 | 9 | 390 | 16.48 | 23.67 | 91.5 | 20 | 9 | 260 | 14.81 | 17.56 | 89.5 | 15 | 9 | 195 | 13.19 | 14.79 | 87.5
100 | 6 | 1300 | 45.21 | 28.76 | 123.5 | 90 | 6 | 1170 | 35.86 | 32.63 | 112.5 | 80 | 6 | 1040 | 29.14 | 35.69 | 105.5 | 70 | 6 | 910.2 | 23.41 | 38.87 | 98.5 | 60 | 6 | 780 | 20.53 | 37.98 | 95.5 | 50 | 6 | 649.9 | 19.07 | 34.08 | 94.5 | 40 | 6 | 520.1 | 17.95 | 28.97 | 93.5 | 30 | 6 | 390 | 16.36 | 23.84 | 91.5 | 20 | 6 | 260 | 14.88 | 17.47 | 89.5 | 15 | 6 | 195 | 13.73 | 14.2 | 88.5
100 | 3 | 1300 | 43.48 | 29.91 | 123.5 | 90 | 3 | 1170 | 34.6 | 33.82 | 112.5 | 80 | 3 | 1040 | 28.83 | 36.08 | 106.5 | 70 | 3 | 910.2 | 23.36 | 38.96 | 99.5 | 60 | 3 | 780 | 20.21 | 38.59 | 95.5 | 50 | 3 | 649.9 | 18.8 | 34.58 | 94.5 | 40 | 3 | 520.1 | 17.97 | 28.95 | 93.5 | 30 | 3 | 390 | 16.33 | 23.88 | 91.5 | 20 | 3 | 260 | 14.56 | 17.86 | 89.5 | 15 | 3 | 195 | 13.14 | 14.85 | 87.5
100 | 0 | 1300 | 42.56 | 30.56 | 123.5 | 90 | 0 | 1170 | 33.9 | 34.51 | 112.5 | 80 | 0 | 1040 | 27.78 | 37.44 | 105.5 | 70 | 0 | 910.2 | 24.29 | 37.47 | 101.5 | 60 | 0 | 780 | 20.02 | 38.97 | 95.5 | 50 | 0 | 649.9 | 18.64 | 34.86 | 94.5 | 40 | 0 | 520.1 | 17.74 | 29.31 | 93.5 | 30 | 0 | 390 | 16.49 | 23.65 | 91.5 | 20 | 0 | 260 | 14.35 | 18.12 | 89.5 | 15 | 0 | 195 | 17.01 | 11.47 | 92.5
100 | -3 | 1300 | 41.86 | 31.07 | 123.5 | 90 | -3 | 1170 | 33.55 | 34.86 | 112.5 | 80 | -3 | 1040 | 29.31 | 35.49 | 107.5 | 70 | -3 | 910.2 | 22.91 | 39.72 | 99.5 | 60 | -3 | 780 | 19.86 | 39.27 | 95.5 | 50 | -3 | 649.9 | 18.54 | 35.06 | 94.5 | 40 | -3 | 520.1 | 17.67 | 29.43 | 93.5 | 30 | -3 | 390 | 16.32 | 23.89 | 91.5 | 20 | -3 | 260 | 14.8 | 17.57 | 89.5
100 | -5 | 1300 | 44.35 | 29.31 | 126.5 | 90 | -5 | 1170 | 34.27 | 34.15 | 113.5 | 80 | -5 | 1040 | 28.1 | 37.01 | 106.5 | 70 | -5 | 910.2 | 23.57 | 38.61 | 100.5 | 60 | -5 | 780 | 19.82 | 39.35 | 95.5 | 50 | -5 | 649.9 | 18.49 | 35.13 | 94.5 | 40 | -5 | 520.1 | 17.64 | 29.48 | 93.5 | 30 | -5 | 390 | 16.35 | 23.86 | 91.5 | 20 | -5 | 260 | 14.37 | 18.09 | 89.5