## Information
Parameter | Value | Unit | Source
Equipment Type | CW Pump | - | Configuration
Model ID | CW_PUMP_6 | - | Configuration
Configuration | ACC_1.5MW_GASENGINE_CDU | - | Configuration
Control Strategy | Single Solver Curve | - | Engineering
Rated Maximum Power | 45 | kW | Engineering Assumption
Curve Method | VFD cubic affinity curve with minimum power allowance | - | Engineering
Notes | Normal and Failure use the same 45 kW equipment curve. Active quantity is handled by Configuration. | - | Engineering

## Metadata
Item | Value
Version | v2.1
Status | Preliminary
Author | ChatGPT
Curve Structure | Single Solver_Curve only
Rated Maximum Power | 45 kW
Validation | Engineering curve placeholder; pending vendor data

## Performance_Map
Operating_Mode | power_kW
Single Curve Rated Power | 45

## Solver_Curve
load_ratio | power_kW
0.1 | 11.28
0.2 | 11.52
0.3 | 12.16
0.4 | 13.41
0.5 | 15.47
0.6 | 18.54
0.7 | 22.83
0.8 | 28.53
0.9 | 35.85
1 | 45

## Validation
Item | Value
Redundancy | Managed by Configuration (N+1)
Equipment Quantity | Not stored in Equipment Package
Curve Structure | One Solver_Curve; no Normal/Failure split
Curve Method | Engineering placeholder: VFD CHW pump cubic affinity curve with minimum power allowance
Formula | power_kW = 45 * (0.25 + 0.75 * load_ratio^3)
Rated Maximum Power | 45 kW at load_ratio = 1.0
Normal / Failure | Same curve used for both scenarios