## Information
Field | Value | Unit / Notes
Equipment ID | DRYCOOLER_6 | Registry ID
Equipment Type | Dry Cooler
Configuration | CHILLER_DRYCOOLER_2MW_GRID_CDU
Cooling System | Chiller + Dry Cooler
Cooling Unit Capacity | 2 | MW
Power Source | Grid
Manufacturer / Source | Dry Cooler SPEC + Coil Calculation Report | Source files provided by user
Manufacturer Model / Code | XXXXA(80+80)061100021WXX(80+80+80+80) | From coil report
Fluid | Water
Design Capacity | 3065 | kW at 44°C ambient from coil report / SPEC table
Design Ambient Air Inlet | 44 | °C
Design Air Outlet | 55.9 | °C from coil report
Design Entering Water | 58 | °C
Design Leaving Water | 52 | °C
Design Water Flow | 444332 | L/h from coil report
Design Water Flow | 444.332 | m³/h
Design Air Flow | 820000 | m³/h
Design Air Pressure Drop | 215 | Pa
Design Coil Pressure Drop | 110 | kPa
Total Pressure Drop | 134 | kPa
Fan Type | Centrifugal | From SPEC
Fan Quantity | 78 | Fans per Dry Cooler
Fan Motor Minimum Power | 3.35 | kW per fan
Nominal Input Power | 261.3 | kW from SPEC
Package Version | v2.0
Data Confidence | Medium | SPEC + coil report available; complete fan curve not provided
Generated By | ChatGPT
Generated Date | 2026-06-30
Temperature-Only Power Curve | Available | Solver_Curve
Curve Input | Outdoor dry-bulb temperature | °C
Curve Output | Single-unit dry cooler input power | kW
Minimum Power | 52.26 | 20% of rated power
Low-Temperature Handling | ≤33°C uses minimum power | No extrapolation below 33°C
High-Temperature Handling | ≥44°C uses rated power | 261.3 kW cap
Curve Limitation | Temperature-only engineering simplification | Load and fan staging excluded

## Metadata
Field | Value | Notes
registry_id | DRYCOOLER_6 | Software equipment ID
equipment_type | dry_cooler | Lowercase type for software use
configuration_name | CHILLER_DRYCOOLER_2MW_GRID_CDU
cooling_system_type | chiller_drycooler
cooling_unit_capacity_mw | 2
power_source | grid
equipment_package_standard | Equipment Package v2.0
excel_role | single_source_for_solver | Excel contains all equipment data
solver_readiness | Partial | Usable with simplified curve; full multi-fan map missing
performance_map_type | ambient_temperature_capacity_map | Dry cooler map
solver_curve_basis | SPEC extended table + coil report design point
source_file_1 | 444T_5852_44C@920G6T80 W320 CHILLER DRY COOLER GRID 6.pdf | Coil calculation report
source_file_2 | Dry Cooler -SPEC V1.0 CHILLER DRY COOLER GRID 6.xlsx | Specification and extended points
solver_curve_type | outdoor_temperature_power | Temperature-only lookup
solver_curve_input | outdoor_dry_bulb_C | °C
solver_curve_output | power_kW | Single-unit input power
minimum_power_kW | 52.26 | 20% rated input
minimum_temperature_C | -10 | Annual EPW lower bound represented
rated_power_cap_kW | 261.3 | Applied at and above 44°C
solver_curve_method | minimum_floor_plus_cubic_affinity_plus_rated_cap | Engineering estimate

## Performance_Map
Source | Ambient_C | Heat_Rejection_kW | Entering_Water_C | Leaving_Water_C | Water_Flow_L_per_h | Water_Flow_m3_per_h | Water_Pressure_Drop_kPa | Air_Flow_m3_per_h | Air_Pressure_Drop_Pa | Fan_Quantity | Fan_Motor_Min_kW_each | Estimated_Total_Fan_Power_kW | Notes
SPEC | 46 | 2532 | 58 | 52 | 366974 | 366.974 | 94.3 | 820000 | 212 | 78 | 3.35 | 261.3 | SPEC operation mode
SPEC | 42 | 3401 | 58 | 49.9 | 366974 | 366.974 | 94.7 | 820000 | 212 | 78 | 3.35 | 261.3 | SPEC operation mode
SPEC | 38.8 | 4107 | 58 | 48.3 | 366974 | 366.974 | 949 | 820000 | 212 | 78 | 3.35 | 261.3 | SPEC lists 949 kPa; likely needs confirmation
Coil Report | 44 | 3065 | 58 | 52 | 444332 | 444.332 | 110 | 820000 | 215 | 78 | 3.35 | 261.3 | Coil calculation report design point
SPEC Extended Table | 33 | 5315 | 58 | 45.51 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=5654 kW, fixed ΔT flow=896382 L/h
SPEC Extended Table | 34 | 5102 | 58 | 46.01 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=5393 kW, fixed ΔT flow=855637 L/h
SPEC Extended Table | 35 | 4890 | 58 | 46.51 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=5131 kW, fixed ΔT flow=814893 L/h
SPEC Extended Table | 36 | 4677 | 58 | 47.01 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=4869 kW, fixed ΔT flow=774148 L/h
SPEC Extended Table | 37 | 4465 | 58 | 47.51 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=4607 kW, fixed ΔT flow=733403 L/h
SPEC Extended Table | 38 | 4252 | 58 | 48.01 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=4345 kW, fixed ΔT flow=692659 L/h
SPEC Extended Table | 39 | 4039 | 58 | 48.5 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=4081 kW, fixed ΔT flow=651914 L/h
SPEC Extended Table | 40 | 3827 | 58 | 49 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=3820 kW, fixed ΔT flow=611170 L/h
SPEC Extended Table | 41 | 3614 | 58 | 49.5 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=3558 kW, fixed ΔT flow=570425 L/h
SPEC Extended Table | 42 | 3402 | 58 | 50 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=3296 kW, fixed ΔT flow=529680 L/h
SPEC Extended Table | 43 | 3189 | 58 | 50.51 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=3034 kW, fixed ΔT flow=488936 L/h
SPEC Extended Table | 44 | 2976 | 58 | 51 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=2777 kW, fixed ΔT flow=448191 L/h
SPEC Extended Table | 45 | 2764 | 58 | 51.5 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=2515 kW, fixed ΔT flow=407446 L/h
SPEC Extended Table | 46 | 2551 | 58 | 52 | 366974 | 366.974 |  | 820000 | 212 | 78 | 3.35 | 261.3 | Fixed flow capacity; fixed ΔT capacity=2551 kW, fixed ΔT flow=366702 L/h

## Solver_Curve
outdoor_dry_bulb_C | power_kW | source_capacity_kW | power_ratio | control_region | solver_use
-10 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
-9 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
-8 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
-7 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
-6 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
-5 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
-4 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
-3 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
-2 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
-1 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
0 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
1 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
2 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
3 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
4 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
5 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
6 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
7 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
8 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
9 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
10 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
11 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
12 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
13 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
14 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
15 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
16 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
17 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
18 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
19 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
20 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
21 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
22 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
23 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
24 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
25 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
26 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
27 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
28 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
29 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
30 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
31 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
32 | 52.26 |  | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
33 | 52.26 | 5315 | 0.2 | Minimum power floor | Temperature-only single-unit power lookup
34 | 56.65 | 5102 | 0.2168 | Cubic affinity estimate | Temperature-only single-unit power lookup
35 | 64.34 | 4890 | 0.2462 | Cubic affinity estimate | Temperature-only single-unit power lookup
36 | 73.54 | 4677 | 0.2814 | Cubic affinity estimate | Temperature-only single-unit power lookup
37 | 84.52 | 4465 | 0.3235 | Cubic affinity estimate | Temperature-only single-unit power lookup
38 | 97.87 | 4252 | 0.3746 | Cubic affinity estimate | Temperature-only single-unit power lookup
39 | 114.19 | 4039 | 0.437 | Cubic affinity estimate | Temperature-only single-unit power lookup
40 | 134.23 | 3827 | 0.5137 | Cubic affinity estimate | Temperature-only single-unit power lookup
41 | 159.39 | 3614 | 0.61 | Cubic affinity estimate | Temperature-only single-unit power lookup
42 | 191.09 | 3402 | 0.7313 | Cubic affinity estimate | Temperature-only single-unit power lookup
43 | 231.99 | 3189 | 0.8878 | Cubic affinity estimate | Temperature-only single-unit power lookup
44 | 261.3 | 2976 | 1 | Rated power cap | Temperature-only single-unit power lookup
45 | 261.3 | 2764 | 1 | Rated power cap | Temperature-only single-unit power lookup
46 | 261.3 | 2551 | 1 | Rated power cap | Temperature-only single-unit power lookup
Curve Notes
Rated dry-cooler input power | 261.3 | kW
Minimum input power assumption | 52.26 | kW | 20% of rated input power
Low-temperature rule | Outdoor temperature ≤ 33°C |  | Use minimum power floor
Intermediate rule | 34°C to 43°C |  | Cubic fan-affinity estimate
High-temperature rule | Outdoor temperature ≥ 44°C |  | Use rated power cap
Model limitation | Temperature-only engineering estimate; actual heat-rejection load, fan staging, water flow and leaving-water control are not modeled.

## Validation
Check Item | Status | Notes
Equipment ID | PASS | DRYCOOLER_6
Required Sheet: Information | PASS
Required Sheet: Metadata | PASS
Required Sheet: Performance_Map | PASS | Includes SPEC points, coil report, and extended table
Required Sheet: Solver_Curve | PASS | Primary fixed-flow curve created from SPEC extended table
Capacity at 44°C | WARNING | SPEC extended fixed-flow table gives 2976 kW; coil report gives 3065 kW at higher water flow
Water Pressure Drop | WARNING | SPEC lists 949 kPa at 38.8°C; likely typo and should be confirmed
Fan Power | PASS | Nominal input power 261.3 kW; derived as 78 fans × 3.35 kW
Temperature-Power Curve | PASS | -10°C to 46°C solver-ready lookup
Minimum Power Floor | PASS | 52.26 kW at ≤33°C
Fan Power Curve | ESTIMATED | Derived from capacity map and cubic affinity
Rated Power Cap | PASS | Maximum 261.3 kW from 44°C upward
Interpolation | PASS | Linear interpolation between listed temperatures
Data Confidence | MEDIUM | Suitable for simplified PUE; not a manufacturer fan-power map