## Information
Parameter | Value | Unit | Source
Equipment Type | RTC | - | Configuration
Model ID | RTC_01_02 | - | Configuration Naming Standard
Configuration | ACC_1.5MW_GASENGINE_CDU | - | Configuration Library
Control Mode | IT Load Ratio Curve | - | Engineering Fit
Reference IT Load | 1000 | kW | Engineering Assumption
Reference RTC Cooling | 150 | kW | Engineering Assumption
Maximum RTC Fan Power | 20 | kW | Engineering Assumption
Low-Load Flat Anchor Ratio | 0.4 | IT Load Ratio | Leadership Review
Fan Power at 40% Anchor | 5 | kW | Engineering Assumption
Fan Power at 10% Low Load | 4.6 | kW | Engineering Assumption
High-Load Curve Exponent | 2 | - | Engineering Fit
Formula Below 40% | Near-flat interpolation from 4.60 kW @10% to 5.00 kW @40% | - | Engineering Fit
Formula Above 40% | P = 5 + (20 - 5) * ((x - 0.40) / (1 - 0.40))^2 | - | Engineering Fit
Notes | RTC fan power is near-flat below 40% IT load ratio, then ramps nonlinearly to 20 kW at full load. | - | Engineering

## Metadata
Item | Value
Version | v1.2
Status | Preliminary Engineering Fit
Author | ChatGPT
Data Source | Engineering assumption revised after leadership review
Validation | Pending vendor performance curve / field test data
Model Scope | RTC fan power curve for PUE Solver software input
Applicable Range | IT Load Ratio 0.10 to 1.00
Curve Intent | Keep RTC fan power nearly flat below 40% IT load ratio
Caution | Do not treat RTC cooling reduction as linear fan power reduction

## Performance_Map
IT_Load_Ratio | RTC_Cooling_kW | Airflow_Ratio | RTC_Fan_Power_kW | Formula_Basis | Notes
0.1 | 15 | 0.1 | 4.6 | Low-load near-flat interpolation | Near-flat low-load region
0.15 | 22.5 | 0.15 | 4.67 | Low-load near-flat interpolation | Near-flat low-load region
0.2 | 30 | 0.2 | 4.73 | Low-load near-flat interpolation | Near-flat low-load region
0.25 | 37.5 | 0.25 | 4.8 | Low-load near-flat interpolation | Near-flat low-load region
0.3 | 45 | 0.3 | 4.87 | Low-load near-flat interpolation | Near-flat low-load region
0.35 | 52.5 | 0.35 | 4.93 | Low-load near-flat interpolation | Near-flat low-load region
0.4 | 60 | 0.4 | 5 | Low-load near-flat interpolation | Flat anchor at 40%
0.5 | 75 | 0.5 | 5.42 | P=5+(20-5)*((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.6 | 90 | 0.6 | 6.67 | P=5+(20-5)*((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.7 | 105 | 0.7 | 8.75 | P=5+(20-5)*((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.8 | 120 | 0.8 | 11.67 | P=5+(20-5)*((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
0.9 | 135 | 0.9 | 15.42 | P=5+(20-5)*((x-0.40)/(1-0.40))^2 | Nonlinear fan-power ramp
1 | 150 | 1 | 20 | P=5+(20-5)*((x-0.40)/(1-0.40))^2 | Maximum power at 100% reference load

## Solver_Curve
load_ratio | power_kW
0.1 | 4.6
0.15 | 4.67
0.2 | 4.73
0.25 | 4.8
0.3 | 4.87
0.35 | 4.93
0.4 | 5
0.5 | 5.42
0.6 | 6.67
0.7 | 8.75
0.8 | 11.67
0.9 | 15.42
1 | 20

## Validation
Item | Value
Curve Type | Near-flat low-load RTC fan curve
Validation Status | Preliminary
Maximum Power | 20 kW at 100% IT Load Ratio
Flat Region Intent | Below 40% IT Load Ratio, fan power changes only slightly
40% Anchor | 5.00 kW
10% Low-Load Estimate | 4.60 kW
High-Load Formula | P = 5 + (20 - 5) * ((x - 0.40) / 0.60)^2
Missing Data | Vendor RTC fan curve / field commissioning data
Future Update | Replace engineering fit with vendor curve when available
Software Read Sheet | Solver_Curve
Software Read Columns | load_ratio, power_kW