## Information
Parameter | Value | Unit | Source / Notes
Equipment Type | Gas Engine | - | Configuration
Model ID | ENGINE_2 | - | Configuration
Configuration | ACC_1.5MW_GASENGINE_CDU | - | Standard package
Engine Output Basis | Group Electrical Power + Electrical System Loss | - | Updated based on leadership scenario summary
Includes Electrical Distribution Loss | Yes | - | Electrical System Loss is included in engine output
Normal Engine Output | 1467.7 | kW per engine | (5740.0 + 130.8) / 4
Failure Engine Output | 1942.9 | kW per engine | (5698.0 + 130.6) / 3
Normal Continuous Power Requirement | 1500 | kW per engine | Leadership scenario summary
Failure Continuous Power Requirement | 1950 | kW per engine | Leadership scenario summary
Control Strategy | Scenario Based Fixed Output | - | Phase 1 simplification
Quantity / Redundancy | Managed by Configuration and Scenario | - | Equipment package stores single-engine performance only

## Metadata
Item | Value
Version | v3.0
Status | Preliminary
Author | ChatGPT
Data Source | Leadership scenario summary screenshot
Last Update | 2026-07-01
Validation | Pending vendor gas engine performance / fuel map
Architecture Note | Equipment package contains single-engine output values only; installed/running unit counts are handled by configuration.xlsx and scenario.xlsx

## Performance_Map
Operating_Mode | Group_Elec_Power_kW | Electrical_System_Loss_kW | Active_Engine_Reference | Engine_Group_Output_kW | Single_Engine_Output_kW | Engine_Continuous_Power_Requirement_kW | Basis
Normal | 5740 | 130.8 | scenario reference only | 5870.8 | 1467.7 | 1500 | (Group Elec Power + ELEC System Loss) / active engines
Failure | 5698 | 130.6 | scenario reference only | 5828.6 | 1942.9 | 1950 | (Group Elec Power + ELEC System Loss) / active engines

## Solver_Curve_Normal
load_ratio | engine_output_kW | engine_continuous_requirement_kW | output_basis
0.1 | 1467.7 | 1500 | Fixed scenario output incl. electrical system loss
0.2 | 1467.7 | 1500 | Fixed scenario output incl. electrical system loss
0.3 | 1467.7 | 1500 | Fixed scenario output incl. electrical system loss
0.4 | 1467.7 | 1500 | Fixed scenario output incl. electrical system loss
0.5 | 1467.7 | 1500 | Fixed scenario output incl. electrical system loss
0.6 | 1467.7 | 1500 | Fixed scenario output incl. electrical system loss
0.7 | 1467.7 | 1500 | Fixed scenario output incl. electrical system loss
0.8 | 1467.7 | 1500 | Fixed scenario output incl. electrical system loss
0.9 | 1467.7 | 1500 | Fixed scenario output incl. electrical system loss
1 | 1467.7 | 1500 | Fixed scenario output incl. electrical system loss

## Solver_Curve_Failure
load_ratio | engine_output_kW | engine_continuous_requirement_kW | output_basis
0.1 | 1942.9 | 1950 | Fixed failure scenario output incl. electrical system loss
0.2 | 1942.9 | 1950 | Fixed failure scenario output incl. electrical system loss
0.3 | 1942.9 | 1950 | Fixed failure scenario output incl. electrical system loss
0.4 | 1942.9 | 1950 | Fixed failure scenario output incl. electrical system loss
0.5 | 1942.9 | 1950 | Fixed failure scenario output incl. electrical system loss
0.6 | 1942.9 | 1950 | Fixed failure scenario output incl. electrical system loss
0.7 | 1942.9 | 1950 | Fixed failure scenario output incl. electrical system loss
0.8 | 1942.9 | 1950 | Fixed failure scenario output incl. electrical system loss
0.9 | 1942.9 | 1950 | Fixed failure scenario output incl. electrical system loss
1 | 1942.9 | 1950 | Fixed failure scenario output incl. electrical system loss

## Validation
Item | Value
Curve Type | Scenario Based Fixed Output
Electrical Loss Included | Yes
Normal Output | 1467.7 kW per engine
Failure Output | 1942.9 kW per engine
Normal Requirement Check | 1467.7 <= 1500 kW
Failure Requirement Check | 1942.9 <= 1950 kW
Redundancy | Managed by Configuration / Scenario, not by this equipment file
Equipment Quantity | Not stored in Equipment Package
Missing Data | Rated engine power; fuel consumption curve; electrical efficiency curve; heat recovery data; emissions data
Future Update | Replace fixed scenario values with vendor gas engine performance / fuel map when available