## Information
Parameter | Value | Unit | Source
Equipment Type | ACC | - | PUE Solver Configuration Library
Equipment ID | ACC_2 | - | User naming
Manufacturer | YORK | - | PDF
Model | YVAM1650 | - | PDF
Cooling Mode | Air Cooled Efficiency Map w/VPF | - | PDF
Refrigerant | R-1234ze | - | PDF
Number of Compressors | 1 | - | PDF
Compressor Type | Variable Speed | - | PDF
Capacity Control | 10% - 100% | - | PDF
Source Temperature Range | 38°C to 55°C | Ambient Dry Bulb | Combined PDFs
Source Load Range | 40% to 100% | Percent Load | Combined PDFs
Software Read Sheet | Solver_Curve | - | PUE Solver Standard
Primary Interpolation Inputs | ambient_C, load_ratio | - | PUE Solver Standard
Primary Outputs | capacity_kW, power_input_kW, unit_efficiency_kW_per_kW | - | PUE Solver Standard

## Metadata
Item | Value
Version | v1.0
Status | Vendor PDF Data Combined
Author | ChatGPT
Created For | ACC_2 / YVAM1650 performance library
Source 1 | YVAM-USA - CH-4 - Performance Report (3).PDF
Source 1 Range | Ambient 38-48°C, Loads 50-100%
Source 2 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF
Source 2 Range | Ambient 49-55°C, Loads 40-100%
Important Note | 40% load points are available only for ambient 49-55°C in the uploaded PDFs.
Validation | Pending vendor confirmation before production calculation use

## Efficiency_Map
Ambient_C | Load_100% | Load_90% | Load_80% | Load_70% | Load_60% | Load_50% | Load_40%
38 | 5.452 | 5.632 | 5.737 | 5.805 | 5.833 | 5.781
40 | 5.058 | 5.209 | 5.293 | 5.326 | 5.347 | 5.262
42 | 4.699 | 4.832 | 4.886 | 4.879 | 4.882 | 4.815
44 | 4.375 | 4.488 | 4.533 | 4.515 | 4.466 | 4.333
46 | 4.062 | 4.165 | 4.199 | 4.186 | 4.138 | 3.995
48 | 3.759 | 3.867 | 3.894 | 3.867 | 3.823 | 3.699
49 | 3.752 | 3.733 | 3.697 | 3.644 | 3.534 | 3.34 | 3.016
50 | 3.616 | 3.594 | 3.562 | 3.51 | 3.395 | 3.206 | 2.909
51 | 3.486 | 3.462 | 3.421 | 3.372 | 3.272 | 3.099 | 2.807
52 | 3.359 | 3.337 | 3.296 | 3.241 | 3.143 | 2.978 | 2.699
53 | 3.241 | 3.215 | 3.18 | 3.121 | 3.024 | 2.864 | 2.599
54 | 3.115 | 3.099 | 3.069 | 3.011 | 2.911 | 2.756 | 2.5
55 | 2.991 | 2.993 | 2.963 | 2.907 | 2.805 | 2.644 | 2.384

## Power_Input_Map
Ambient_C | Load_100% | Load_90% | Load_80% | Load_70% | Load_60% | Load_50% | Load_40%
38 | 294.8 | 256.9 | 224.1 | 193.8 | 165.3 | 139
40 | 317.7 | 277.7 | 242.9 | 211.2 | 180.3 | 152.7
42 | 342 | 299.4 | 263.2 | 230.6 | 197.5 | 166.9
44 | 367.4 | 322.3 | 283.7 | 249.2 | 215.9 | 185.5
46 | 395.7 | 347.3 | 306.2 | 268.8 | 233 | 201.2
48 | 427.5 | 374 | 330.2 | 291 | 252.3 | 217.2
49 | 350.4 | 317 | 284.5 | 252.5 | 223.2 | 196.7 | 174.4
50 | 363.5 | 329.2 | 295.3 | 262.2 | 232.4 | 205 | 180.7
51 | 377.1 | 341.7 | 307.2 | 272.9 | 241.1 | 212.1 | 187.4
52 | 391.2 | 354.6 | 319 | 283.8 | 250.9 | 220.8 | 194.7
53 | 405.6 | 368.1 | 330.8 | 294.9 | 260.8 | 229.5 | 202.3
54 | 422.1 | 381.8 | 342.7 | 305.6 | 271 | 238.5 | 210.4
55 | 439.5 | 395.2 | 355.1 | 316.7 | 281.2 | 248.6 | 220.5

## Capacity_Map
Ambient_C | Load_100% | Load_90% | Load_80% | Load_70% | Load_60% | Load_50% | Load_40%
38 | 1607 | 1447 | 1286 | 1125 | 964.4 | 803.6
40 | 1607 | 1447 | 1286 | 1125 | 964.4 | 803.6
42 | 1607 | 1447 | 1286 | 1125 | 964.4 | 803.6
44 | 1607 | 1447 | 1286 | 1125 | 964.4 | 803.6
46 | 1607 | 1447 | 1286 | 1125 | 964.4 | 803.6
48 | 1607 | 1447 | 1286 | 1125 | 964.4 | 803.6
49 | 1314 | 1183 | 1052 | 920.1 | 788.7 | 657.2 | 525.8
50 | 1314 | 1183 | 1052 | 920.1 | 788.7 | 657.2 | 525.8
51 | 1314 | 1183 | 1052 | 920.1 | 788.7 | 657.2 | 525.8
52 | 1314 | 1183 | 1052 | 920.1 | 788.7 | 657.2 | 525.8
53 | 1314 | 1183 | 1052 | 920.1 | 788.7 | 657.2 | 525.8
54 | 1314 | 1183 | 1052 | 920.1 | 788.7 | 657.2 | 525.8
55 | 1314 | 1183 | 1052 | 920.1 | 788.7 | 657.2 | 525.8

## Performance_Map
percent_load | load_ratio | ambient_C | capacity_kW | power_input_kW | unit_efficiency_kW_per_kW | EFT_C | LFT_C | flow_rate_L_s | evap_PD_kPa | source_document | source_page | source_range
100 | 1 | 48 | 1607 | 427.5 | 3.759 | 32 | 22 | 40.16 | 35 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
100 | 1 | 46 | 1607 | 395.7 | 4.062 | 32 | 22 | 40.16 | 35 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
100 | 1 | 44 | 1607 | 367.4 | 4.375 | 32 | 22 | 40.16 | 35 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
100 | 1 | 42 | 1607 | 342 | 4.699 | 32 | 22 | 40.16 | 35 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
100 | 1 | 40 | 1607 | 317.7 | 5.058 | 32 | 22 | 40.16 | 35 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
100 | 1 | 38 | 1607 | 294.8 | 5.452 | 32 | 22 | 40.16 | 35 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
90 | 0.9 | 48 | 1447 | 374 | 3.867 | 32 | 22 | 36.15 | 28.6 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
90 | 0.9 | 46 | 1447 | 347.3 | 4.165 | 32 | 22 | 36.15 | 28.6 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
90 | 0.9 | 44 | 1447 | 322.3 | 4.488 | 32 | 22 | 36.15 | 28.6 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
90 | 0.9 | 42 | 1447 | 299.4 | 4.832 | 32 | 22 | 36.15 | 28.6 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
90 | 0.9 | 40 | 1447 | 277.7 | 5.209 | 32 | 22 | 36.15 | 28.6 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
90 | 0.9 | 38 | 1447 | 256.9 | 5.632 | 32 | 22 | 36.15 | 28.6 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
80 | 0.8 | 48 | 1286 | 330.2 | 3.894 | 32 | 22 | 32.13 | 22.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
80 | 0.8 | 46 | 1286 | 306.2 | 4.199 | 32 | 22 | 32.13 | 22.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
80 | 0.8 | 44 | 1286 | 283.7 | 4.533 | 32 | 22 | 32.13 | 22.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
80 | 0.8 | 42 | 1286 | 263.2 | 4.886 | 32 | 22 | 32.13 | 22.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
80 | 0.8 | 40 | 1286 | 242.9 | 5.293 | 32 | 22 | 32.13 | 22.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
80 | 0.8 | 38 | 1286 | 224.1 | 5.737 | 32 | 22 | 32.13 | 22.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
70 | 0.7 | 48 | 1125 | 291 | 3.867 | 31.39 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
70 | 0.7 | 46 | 1125 | 268.8 | 4.186 | 31.39 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
70 | 0.7 | 44 | 1125 | 249.2 | 4.515 | 31.39 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
70 | 0.7 | 42 | 1125 | 230.6 | 4.879 | 31.39 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
70 | 0.7 | 40 | 1125 | 211.2 | 5.326 | 31.39 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
70 | 0.7 | 38 | 1125 | 193.8 | 5.805 | 31.39 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
60 | 0.6 | 48 | 964.4 | 252.3 | 3.823 | 30.05 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
60 | 0.6 | 46 | 964.4 | 233 | 4.138 | 30.05 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
60 | 0.6 | 44 | 964.4 | 215.9 | 4.466 | 30.05 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
60 | 0.6 | 42 | 964.4 | 197.5 | 4.882 | 30.05 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
60 | 0.6 | 40 | 964.4 | 180.3 | 5.347 | 30.05 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
60 | 0.6 | 38 | 964.4 | 165.3 | 5.833 | 30.05 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
50 | 0.5 | 48 | 803.6 | 217.2 | 3.699 | 28.71 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
50 | 0.5 | 46 | 803.6 | 201.2 | 3.995 | 28.71 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
50 | 0.5 | 44 | 803.6 | 185.5 | 4.333 | 28.71 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
50 | 0.5 | 42 | 803.6 | 166.9 | 4.815 | 28.71 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
50 | 0.5 | 40 | 803.6 | 152.7 | 5.262 | 28.71 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
50 | 0.5 | 38 | 803.6 | 139 | 5.781 | 28.71 | 22 | 29.95 | 19.7 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 3 | 38-48C
100 | 1 | 55 | 1314 | 439.5 | 2.991 | 32 | 22 | 32.85 | 23.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
100 | 1 | 54 | 1314 | 422.1 | 3.115 | 32 | 22 | 32.85 | 23.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
100 | 1 | 53 | 1314 | 405.6 | 3.241 | 32 | 22 | 32.85 | 23.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
100 | 1 | 52 | 1314 | 391.2 | 3.359 | 32 | 22 | 32.85 | 23.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
100 | 1 | 51 | 1314 | 377.1 | 3.486 | 32 | 22 | 32.85 | 23.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
100 | 1 | 50 | 1314 | 363.5 | 3.616 | 32 | 22 | 32.85 | 23.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
100 | 1 | 49 | 1314 | 350.4 | 3.752 | 32 | 22 | 32.85 | 23.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
90 | 0.9 | 55 | 1183 | 395.2 | 2.993 | 31.87 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
90 | 0.9 | 54 | 1183 | 381.8 | 3.099 | 31.87 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
90 | 0.9 | 53 | 1183 | 368.1 | 3.215 | 31.87 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
90 | 0.9 | 52 | 1183 | 354.6 | 3.337 | 31.87 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
90 | 0.9 | 51 | 1183 | 341.7 | 3.462 | 31.87 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
90 | 0.9 | 50 | 1183 | 329.2 | 3.594 | 31.87 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
90 | 0.9 | 49 | 1183 | 317 | 3.733 | 31.87 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
80 | 0.8 | 55 | 1052 | 355.1 | 2.963 | 30.78 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
80 | 0.8 | 54 | 1052 | 342.7 | 3.069 | 30.78 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
80 | 0.8 | 53 | 1052 | 330.8 | 3.18 | 30.78 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
80 | 0.8 | 52 | 1052 | 319 | 3.296 | 30.78 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
80 | 0.8 | 51 | 1052 | 307.2 | 3.421 | 30.78 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
80 | 0.8 | 50 | 1052 | 295.3 | 3.562 | 30.78 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
80 | 0.8 | 49 | 1052 | 284.5 | 3.697 | 30.78 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
70 | 0.7 | 55 | 920.1 | 316.7 | 2.907 | 29.68 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
70 | 0.7 | 54 | 920.1 | 305.6 | 3.011 | 29.68 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
70 | 0.7 | 53 | 920.1 | 294.9 | 3.121 | 29.68 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
70 | 0.7 | 52 | 920.1 | 283.8 | 3.241 | 29.68 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
70 | 0.7 | 51 | 920.1 | 272.9 | 3.372 | 29.68 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
70 | 0.7 | 50 | 920.1 | 262.2 | 3.51 | 29.68 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
70 | 0.7 | 49 | 920.1 | 252.5 | 3.644 | 29.68 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
60 | 0.6 | 55 | 788.7 | 281.2 | 2.805 | 28.58 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
60 | 0.6 | 54 | 788.7 | 271 | 2.911 | 28.58 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
60 | 0.6 | 53 | 788.7 | 260.8 | 3.024 | 28.58 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
60 | 0.6 | 52 | 788.7 | 250.9 | 3.143 | 28.58 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
60 | 0.6 | 51 | 788.7 | 241.1 | 3.272 | 28.58 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
60 | 0.6 | 50 | 788.7 | 232.4 | 3.395 | 28.58 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
60 | 0.6 | 49 | 788.7 | 223.2 | 3.534 | 28.58 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3 | 49-55C
50 | 0.5 | 55 | 657.2 | 248.6 | 2.644 | 27.49 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
50 | 0.5 | 54 | 657.2 | 238.5 | 2.756 | 27.49 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
50 | 0.5 | 53 | 657.2 | 229.5 | 2.864 | 27.49 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
50 | 0.5 | 52 | 657.2 | 220.8 | 2.978 | 27.49 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
50 | 0.5 | 51 | 657.2 | 212.1 | 3.099 | 27.49 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
50 | 0.5 | 50 | 657.2 | 205 | 3.206 | 27.49 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
50 | 0.5 | 49 | 657.2 | 196.7 | 3.34 | 27.49 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
40 | 0.4 | 55 | 525.8 | 220.5 | 2.384 | 26.39 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
40 | 0.4 | 54 | 525.8 | 210.4 | 2.5 | 26.39 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
40 | 0.4 | 53 | 525.8 | 202.3 | 2.599 | 26.39 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
40 | 0.4 | 52 | 525.8 | 194.7 | 2.699 | 26.39 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
40 | 0.4 | 51 | 525.8 | 187.4 | 2.807 | 26.39 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
40 | 0.4 | 50 | 525.8 | 180.7 | 2.909 | 26.39 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C
40 | 0.4 | 49 | 525.8 | 174.4 | 3.016 | 26.39 | 22 | 29.95 | 19.7 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 3-4 | 49-55C

## Solver_Curve
ambient_C | load_ratio | capacity_kW | power_input_kW | unit_efficiency_kW_per_kW | source_range
-10 | 1 | 1607 | 106.1 | 15.146 | estimated_low_ambient
-10 | 0.9 | 1447 | 92.5 | 15.643 | estimated_low_ambient
-10 | 0.8 | 1286 | 80.7 | 15.936 | estimated_low_ambient
-10 | 0.7 | 1125 | 69.8 | 16.117 | estimated_low_ambient
-10 | 0.6 | 964.4 | 59.5 | 16.208 | estimated_low_ambient
-10 | 0.5 | 803.6 | 50 | 16.072 | estimated_low_ambient
-5 | 1 | 1607 | 115 | 13.974 | estimated_low_ambient
-5 | 0.9 | 1447 | 100.2 | 14.441 | estimated_low_ambient
-5 | 0.8 | 1286 | 87.4 | 14.714 | estimated_low_ambient
-5 | 0.7 | 1125 | 75.6 | 14.881 | estimated_low_ambient
-5 | 0.6 | 964.4 | 64.5 | 14.952 | estimated_low_ambient
-5 | 0.5 | 803.6 | 54.2 | 14.827 | estimated_low_ambient
0 | 1 | 1607 | 123.8 | 12.981 | estimated_low_ambient
0 | 0.9 | 1447 | 107.9 | 13.411 | estimated_low_ambient
0 | 0.8 | 1286 | 94.1 | 13.666 | estimated_low_ambient
0 | 0.7 | 1125 | 81.4 | 13.821 | estimated_low_ambient
0 | 0.6 | 964.4 | 69.4 | 13.896 | estimated_low_ambient
0 | 0.5 | 803.6 | 58.4 | 13.76 | estimated_low_ambient
5 | 1 | 1607 | 135.6 | 11.851 | estimated_low_ambient
5 | 0.9 | 1447 | 118.2 | 12.242 | estimated_low_ambient
5 | 0.8 | 1286 | 103.1 | 12.473 | estimated_low_ambient
5 | 0.7 | 1125 | 89.1 | 12.626 | estimated_low_ambient
5 | 0.6 | 964.4 | 76 | 12.689 | estimated_low_ambient
5 | 0.5 | 803.6 | 63.9 | 12.576 | estimated_low_ambient
10 | 1 | 1607 | 150.3 | 10.691 | estimated_low_ambient
10 | 0.9 | 1447 | 131 | 11.046 | estimated_low_ambient
10 | 0.8 | 1286 | 114.3 | 11.251 | estimated_low_ambient
10 | 0.7 | 1125 | 98.8 | 11.387 | estimated_low_ambient
10 | 0.6 | 964.4 | 84.3 | 11.44 | estimated_low_ambient
10 | 0.5 | 803.6 | 70.9 | 11.334 | estimated_low_ambient
15 | 1 | 1607 | 168 | 9.565 | estimated_low_ambient
15 | 0.9 | 1447 | 146.4 | 9.884 | estimated_low_ambient
15 | 0.8 | 1286 | 127.7 | 10.07 | estimated_low_ambient
15 | 0.7 | 1125 | 110.5 | 10.181 | estimated_low_ambient
15 | 0.6 | 964.4 | 94.2 | 10.238 | estimated_low_ambient
15 | 0.5 | 803.6 | 79.2 | 10.146 | estimated_low_ambient
20 | 1 | 1607 | 188.7 | 8.516 | estimated_low_ambient
20 | 0.9 | 1447 | 164.4 | 8.802 | estimated_low_ambient
20 | 0.8 | 1286 | 143.4 | 8.968 | estimated_low_ambient
20 | 0.7 | 1125 | 124 | 9.073 | estimated_low_ambient
20 | 0.6 | 964.4 | 105.8 | 9.115 | estimated_low_ambient
20 | 0.5 | 803.6 | 89 | 9.029 | estimated_low_ambient
25 | 1 | 1607 | 212.3 | 7.57 | estimated_low_ambient
25 | 0.9 | 1447 | 185 | 7.822 | estimated_low_ambient
25 | 0.8 | 1286 | 161.4 | 7.968 | estimated_low_ambient
25 | 0.7 | 1125 | 139.5 | 8.065 | estimated_low_ambient
25 | 0.6 | 964.4 | 119 | 8.104 | estimated_low_ambient
25 | 0.5 | 803.6 | 100.1 | 8.028 | estimated_low_ambient
30 | 1 | 1607 | 241.7 | 6.649 | estimated_low_ambient
30 | 0.9 | 1447 | 210.7 | 6.868 | estimated_low_ambient
30 | 0.8 | 1286 | 183.8 | 6.997 | estimated_low_ambient
30 | 0.7 | 1125 | 158.9 | 7.08 | estimated_low_ambient
30 | 0.6 | 964.4 | 135.5 | 7.117 | estimated_low_ambient
30 | 0.5 | 803.6 | 114 | 7.049 | estimated_low_ambient
35 | 1 | 1607 | 274.2 | 5.861 | estimated_low_ambient
35 | 0.9 | 1447 | 238.9 | 6.057 | estimated_low_ambient
35 | 0.8 | 1286 | 208.4 | 6.171 | estimated_low_ambient
35 | 0.7 | 1125 | 180.2 | 6.243 | estimated_low_ambient
35 | 0.6 | 964.4 | 153.7 | 6.275 | estimated_low_ambient
35 | 0.5 | 803.6 | 129.3 | 6.215 | estimated_low_ambient
38 | 1 | 1607 | 294.8 | 5.452 | 38-48C
38 | 0.9 | 1447 | 256.9 | 5.632 | 38-48C
38 | 0.8 | 1286 | 224.1 | 5.737 | 38-48C
38 | 0.7 | 1125 | 193.8 | 5.805 | 38-48C
38 | 0.6 | 964.4 | 165.3 | 5.833 | 38-48C
38 | 0.5 | 803.6 | 139 | 5.781 | 38-48C
40 | 1 | 1607 | 317.7 | 5.058 | 38-48C
40 | 0.9 | 1447 | 277.7 | 5.209 | 38-48C
40 | 0.8 | 1286 | 242.9 | 5.293 | 38-48C
40 | 0.7 | 1125 | 211.2 | 5.326 | 38-48C
40 | 0.6 | 964.4 | 180.3 | 5.347 | 38-48C
40 | 0.5 | 803.6 | 152.7 | 5.262 | 38-48C
42 | 1 | 1607 | 342 | 4.699 | 38-48C
42 | 0.9 | 1447 | 299.4 | 4.832 | 38-48C
42 | 0.8 | 1286 | 263.2 | 4.886 | 38-48C
42 | 0.7 | 1125 | 230.6 | 4.879 | 38-48C
42 | 0.6 | 964.4 | 197.5 | 4.882 | 38-48C
42 | 0.5 | 803.6 | 166.9 | 4.815 | 38-48C
44 | 1 | 1616 | 386 | 4.375 | 38-48C
44 | 0.9 | 1447 | 322.3 | 4.488 | 38-48C
44 | 0.8 | 1286 | 283.7 | 4.533 | 38-48C
44 | 0.7 | 1125 | 249.2 | 4.515 | 38-48C
44 | 0.6 | 964.4 | 215.9 | 4.466 | 38-48C
44 | 0.5 | 803.6 | 185.5 | 4.333 | 38-48C
46 | 1 | 1607 | 395.7 | 4.062 | 38-48C
46 | 0.9 | 1447 | 347.3 | 4.165 | 38-48C
46 | 0.8 | 1286 | 306.2 | 4.199 | 38-48C
46 | 0.7 | 1125 | 268.8 | 4.186 | 38-48C
46 | 0.6 | 964.4 | 233 | 4.138 | 38-48C
46 | 0.5 | 803.6 | 201.2 | 3.995 | 38-48C
48 | 1 | 1607 | 427.5 | 3.759 | 38-48C
48 | 0.9 | 1447 | 374 | 3.867 | 38-48C
48 | 0.8 | 1286 | 330.2 | 3.894 | 38-48C
48 | 0.7 | 1125 | 291 | 3.867 | 38-48C
48 | 0.6 | 964.4 | 252.3 | 3.823 | 38-48C
48 | 0.5 | 803.6 | 217.2 | 3.699 | 38-48C
49 | 1 | 1314 | 350.4 | 3.752 | 49-55C
49 | 0.9 | 1183 | 317 | 3.733 | 49-55C
49 | 0.8 | 1052 | 284.5 | 3.697 | 49-55C
49 | 0.7 | 920.1 | 252.5 | 3.644 | 49-55C
49 | 0.6 | 788.7 | 223.2 | 3.534 | 49-55C
49 | 0.5 | 657.2 | 196.7 | 3.34 | 49-55C
50 | 1 | 1314 | 363.5 | 3.616 | 49-55C
50 | 0.9 | 1183 | 329.2 | 3.594 | 49-55C
50 | 0.8 | 1052 | 295.3 | 3.562 | 49-55C
50 | 0.7 | 920.1 | 262.2 | 3.51 | 49-55C
50 | 0.6 | 788.7 | 232.4 | 3.395 | 49-55C
50 | 0.5 | 657.2 | 205 | 3.206 | 49-55C
51 | 1 | 1314 | 377.1 | 3.486 | 49-55C
51 | 0.9 | 1183 | 341.7 | 3.462 | 49-55C
51 | 0.8 | 1052 | 307.2 | 3.421 | 49-55C
51 | 0.7 | 920.1 | 272.9 | 3.372 | 49-55C
51 | 0.6 | 788.7 | 241.1 | 3.272 | 49-55C
51 | 0.5 | 657.2 | 212.1 | 3.099 | 49-55C
52 | 1 | 1314 | 391.2 | 3.359 | 49-55C
52 | 0.9 | 1183 | 354.6 | 3.337 | 49-55C
52 | 0.8 | 1052 | 319 | 3.296 | 49-55C
52 | 0.7 | 920.1 | 283.8 | 3.241 | 49-55C
52 | 0.6 | 788.7 | 250.9 | 3.143 | 49-55C
52 | 0.5 | 657.2 | 220.8 | 2.978 | 49-55C
53 | 1 | 1314 | 405.6 | 3.241 | 49-55C
53 | 0.9 | 1183 | 368.1 | 3.215 | 49-55C
53 | 0.8 | 1052 | 330.8 | 3.18 | 49-55C
53 | 0.7 | 920.1 | 294.9 | 3.121 | 49-55C
53 | 0.6 | 788.7 | 260.8 | 3.024 | 49-55C
53 | 0.5 | 657.2 | 229.5 | 2.864 | 49-55C
54 | 1 | 1314 | 422.1 | 3.115 | 49-55C
54 | 0.9 | 1183 | 381.8 | 3.099 | 49-55C
54 | 0.8 | 1052 | 342.7 | 3.069 | 49-55C
54 | 0.7 | 920.1 | 305.6 | 3.011 | 49-55C
54 | 0.6 | 788.7 | 271 | 2.911 | 49-55C
54 | 0.5 | 657.2 | 238.5 | 2.756 | 49-55C
55 | 1 | 1314 | 439.5 | 2.991 | 49-55C
55 | 0.9 | 1183 | 395.2 | 2.993 | 49-55C
55 | 0.8 | 1052 | 355.1 | 2.963 | 49-55C
55 | 0.7 | 920.1 | 316.7 | 2.907 | 49-55C
55 | 0.6 | 788.7 | 281.2 | 2.805 | 49-55C
55 | 0.5 | 657.2 | 248.6 | 2.644 | 49-55C

## Condenser_Performance
percent_load | load_ratio | ambient_C | heat_rejection_kW | discharge_air_temp_C | total_air_flow_m3_s | active_fans | source_document | source_page | source_range
100 | 1 | 48 | 1998 | 56.17 | 207 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
100 | 1 | 46 | 1978 | 54.78 | 192 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
100 | 1 | 44 | 1953 | 53.06 | 184 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
100 | 1 | 42 | 1928 | 51.06 | 181 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
100 | 1 | 40 | 1908 | 49.33 | 174 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
100 | 1 | 38 | 1885 | 47.33 | 172 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
90 | 0.9 | 48 | 1795 | 56.28 | 183 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
90 | 0.9 | 46 | 1773 | 54.61 | 175 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
90 | 0.9 | 44 | 1748 | 52.61 | 173 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
90 | 0.9 | 42 | 1726 | 50.61 | 170 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
90 | 0.9 | 40 | 1704 | 48.61 | 168 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
90 | 0.9 | 38 | 1686 | 46.89 | 161 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
80 | 0.8 | 48 | 1590 | 55.72 | 174 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
80 | 0.8 | 46 | 1568 | 53.89 | 169 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
80 | 0.8 | 44 | 1549 | 52.17 | 162 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
80 | 0.8 | 42 | 1528 | 50.06 | 162 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
80 | 0.8 | 40 | 1510 | 48.17 | 158 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
80 | 0.8 | 38 | 1490 | 46.17 | 156 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
70 | 0.7 | 48 | 1390 | 55.11 | 165 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
70 | 0.7 | 46 | 1369 | 53.17 | 163 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
70 | 0.7 | 44 | 1354 | 51.5 | 154 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
70 | 0.7 | 42 | 1332 | 49.17 | 158 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
70 | 0.7 | 40 | 1315 | 47.28 | 154 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
70 | 0.7 | 38 | 1301 | 45.61 | 145 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
60 | 0.6 | 48 | 1192 | 54.5 | 156 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
60 | 0.6 | 46 | 1177 | 52.83 | 147 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
60 | 0.6 | 44 | 1161 | 50.83 | 145 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
60 | 0.6 | 42 | 1142 | 48.72 | 145 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
60 | 0.6 | 40 | 1128 | 47.06 | 136 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
60 | 0.6 | 38 | 1113 | 44.94 | 137 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 48 | 1002 | 54.06 | 140 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 46 | 986.4 | 52.06 | 138 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 44 | 971.3 | 50.06 | 136 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 42 | 954.3 | 48.17 | 131 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 40 | 941.4 | 46.28 | 128 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
50 | 0.5 | 38 | 927.4 | 44.17 | 128 | 26 | YVAM-USA - CH-4 - Performance Report (3).PDF | Page 4 | 38-48C
100 | 1 | 55 | 1708 | 61.89 | 207 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 54 | 1697 | 61.17 | 198 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 53 | 1690 | 60.61 | 186 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 52 | 1678 | 59.72 | 182 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 51 | 1664 | 58.78 | 181 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 50 | 1651 | 57.78 | 179 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
100 | 1 | 49 | 1638 | 56.78 | 178 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 55 | 1548 | 62.17 | 180 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 54 | 1535 | 61.22 | 179 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 53 | 1525 | 60.44 | 172 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 52 | 1511 | 59.39 | 173 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 51 | 1499 | 58.39 | 171 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 50 | 1485 | 57.28 | 172 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
90 | 0.9 | 49 | 1475 | 56.39 | 168 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 55 | 1379 | 61.78 | 170 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 54 | 1368 | 60.89 | 166 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 53 | 1355 | 59.83 | 167 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 52 | 1344 | 58.83 | 166 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 51 | 1335 | 58.06 | 160 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 50 | 1322 | 56.94 | 161 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
80 | 0.8 | 49 | 1311 | 55.89 | 161 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 55 | 1213 | 61.44 | 158 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 54 | 1202 | 60.44 | 156 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 53 | 1191 | 59.39 | 157 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 52 | 1179 | 58.28 | 158 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 51 | 1169 | 57.39 | 155 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 50 | 1162 | 56.72 | 147 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
70 | 0.7 | 49 | 1151 | 55.5 | 150 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 55 | 1048 | 60.89 | 150 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 54 | 1038 | 59.89 | 148 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 53 | 1029 | 58.94 | 145 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 52 | 1018 | 57.78 | 148 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 51 | 1008 | 56.83 | 147 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 50 | 1000 | 55.83 | 145 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
60 | 0.6 | 49 | 992.1 | 54.89 | 142 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5 | 49-55C
50 | 0.5 | 55 | 885.2 | 60.22 | 143 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 54 | 877.1 | 59.33 | 138 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 53 | 867.7 | 58.28 | 139 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 52 | 858.6 | 57.22 | 139 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 51 | 851.7 | 56.39 | 134 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 50 | 844.9 | 55.39 | 133 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
50 | 0.5 | 49 | 837 | 54.39 | 132 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 55 | 726.8 | 59.44 | 138 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 54 | 720.4 | 58.78 | 127 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 53 | 712.5 | 57.78 | 127 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 52 | 705.1 | 56.72 | 126 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 51 | 698.9 | 55.83 | 122 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 50 | 695.6 | 55.33 | 111 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C
40 | 0.4 | 49 | 685.7 | 53.78 | 123 | 26 | 002-AMB 55-49C-YVAM-USA - CH-4 - Performance Report.PDF | Page 5-6 | 49-55C

## Validation
Item | Value
Formula errors scan | Pass
Model | YVAM1650
Combined ambient points | 38, 40, 42, 44, 46, 48, 49, 50, 51, 52, 53, 54, 55°C
Combined load points | 40%, 50%, 60%, 70%, 80%, 90%, 100%
Missing 40% load at 38-48°C | Yes - not present in uploaded PDF
Recommended solver behavior | Use 2D interpolation within available grid; clamp or fallback only when outside source range.
Do not double count | Power_Input_kW is total unit input power from vendor table.
Source 1 citation | PDF page 2-4: 38-48°C performance and condenser tables
Source 2 citation | PDF page 2-6: 49-55°C performance and condenser tables

## Solver_Curve_Original
ambient_C | load_ratio | capacity_kW | power_input_kW | unit_efficiency_kW_per_kW | source_range
48 | 1 | 1607 | 427.5 | 3.759 | 38-48C
46 | 1 | 1607 | 395.7 | 4.062 | 38-48C
44 | 1 | 1607 | 367.4 | 4.375 | 38-48C
42 | 1 | 1607 | 342 | 4.699 | 38-48C
40 | 1 | 1607 | 317.7 | 5.058 | 38-48C
38 | 1 | 1607 | 294.8 | 5.452 | 38-48C
48 | 0.9 | 1447 | 374 | 3.867 | 38-48C
46 | 0.9 | 1447 | 347.3 | 4.165 | 38-48C
44 | 0.9 | 1447 | 322.3 | 4.488 | 38-48C
42 | 0.9 | 1447 | 299.4 | 4.832 | 38-48C
40 | 0.9 | 1447 | 277.7 | 5.209 | 38-48C
38 | 0.9 | 1447 | 256.9 | 5.632 | 38-48C
48 | 0.8 | 1286 | 330.2 | 3.894 | 38-48C
46 | 0.8 | 1286 | 306.2 | 4.199 | 38-48C
44 | 0.8 | 1286 | 283.7 | 4.533 | 38-48C
42 | 0.8 | 1286 | 263.2 | 4.886 | 38-48C
40 | 0.8 | 1286 | 242.9 | 5.293 | 38-48C
38 | 0.8 | 1286 | 224.1 | 5.737 | 38-48C
48 | 0.7 | 1125 | 291 | 3.867 | 38-48C
46 | 0.7 | 1125 | 268.8 | 4.186 | 38-48C
44 | 0.7 | 1125 | 249.2 | 4.515 | 38-48C
42 | 0.7 | 1125 | 230.6 | 4.879 | 38-48C
40 | 0.7 | 1125 | 211.2 | 5.326 | 38-48C
38 | 0.7 | 1125 | 193.8 | 5.805 | 38-48C
48 | 0.6 | 964.4 | 252.3 | 3.823 | 38-48C
46 | 0.6 | 964.4 | 233 | 4.138 | 38-48C
44 | 0.6 | 964.4 | 215.9 | 4.466 | 38-48C
42 | 0.6 | 964.4 | 197.5 | 4.882 | 38-48C
40 | 0.6 | 964.4 | 180.3 | 5.347 | 38-48C
38 | 0.6 | 964.4 | 165.3 | 5.833 | 38-48C
48 | 0.5 | 803.6 | 217.2 | 3.699 | 38-48C
46 | 0.5 | 803.6 | 201.2 | 3.995 | 38-48C
44 | 0.5 | 803.6 | 185.5 | 4.333 | 38-48C
42 | 0.5 | 803.6 | 166.9 | 4.815 | 38-48C
40 | 0.5 | 803.6 | 152.7 | 5.262 | 38-48C
38 | 0.5 | 803.6 | 139 | 5.781 | 38-48C
55 | 1 | 1314 | 439.5 | 2.991 | 49-55C
54 | 1 | 1314 | 422.1 | 3.115 | 49-55C
53 | 1 | 1314 | 405.6 | 3.241 | 49-55C
52 | 1 | 1314 | 391.2 | 3.359 | 49-55C
51 | 1 | 1314 | 377.1 | 3.486 | 49-55C
50 | 1 | 1314 | 363.5 | 3.616 | 49-55C
49 | 1 | 1314 | 350.4 | 3.752 | 49-55C
55 | 0.9 | 1183 | 395.2 | 2.993 | 49-55C
54 | 0.9 | 1183 | 381.8 | 3.099 | 49-55C
53 | 0.9 | 1183 | 368.1 | 3.215 | 49-55C
52 | 0.9 | 1183 | 354.6 | 3.337 | 49-55C
51 | 0.9 | 1183 | 341.7 | 3.462 | 49-55C
50 | 0.9 | 1183 | 329.2 | 3.594 | 49-55C
49 | 0.9 | 1183 | 317 | 3.733 | 49-55C
55 | 0.8 | 1052 | 355.1 | 2.963 | 49-55C
54 | 0.8 | 1052 | 342.7 | 3.069 | 49-55C
53 | 0.8 | 1052 | 330.8 | 3.18 | 49-55C
52 | 0.8 | 1052 | 319 | 3.296 | 49-55C
51 | 0.8 | 1052 | 307.2 | 3.421 | 49-55C
50 | 0.8 | 1052 | 295.3 | 3.562 | 49-55C
49 | 0.8 | 1052 | 284.5 | 3.697 | 49-55C
55 | 0.7 | 920.1 | 316.7 | 2.907 | 49-55C
54 | 0.7 | 920.1 | 305.6 | 3.011 | 49-55C
53 | 0.7 | 920.1 | 294.9 | 3.121 | 49-55C
52 | 0.7 | 920.1 | 283.8 | 3.241 | 49-55C
51 | 0.7 | 920.1 | 272.9 | 3.372 | 49-55C
50 | 0.7 | 920.1 | 262.2 | 3.51 | 49-55C
49 | 0.7 | 920.1 | 252.5 | 3.644 | 49-55C
55 | 0.6 | 788.7 | 281.2 | 2.805 | 49-55C
54 | 0.6 | 788.7 | 271 | 2.911 | 49-55C
53 | 0.6 | 788.7 | 260.8 | 3.024 | 49-55C
52 | 0.6 | 788.7 | 250.9 | 3.143 | 49-55C
51 | 0.6 | 788.7 | 241.1 | 3.272 | 49-55C
50 | 0.6 | 788.7 | 232.4 | 3.395 | 49-55C
49 | 0.6 | 788.7 | 223.2 | 3.534 | 49-55C
55 | 0.5 | 657.2 | 248.6 | 2.644 | 49-55C
54 | 0.5 | 657.2 | 238.5 | 2.756 | 49-55C
53 | 0.5 | 657.2 | 229.5 | 2.864 | 49-55C
52 | 0.5 | 657.2 | 220.8 | 2.978 | 49-55C
51 | 0.5 | 657.2 | 212.1 | 3.099 | 49-55C
50 | 0.5 | 657.2 | 205 | 3.206 | 49-55C
49 | 0.5 | 657.2 | 196.7 | 3.34 | 49-55C
55 | 0.4 | 525.8 | 220.5 | 2.384 | 49-55C
54 | 0.4 | 525.8 | 210.4 | 2.5 | 49-55C
53 | 0.4 | 525.8 | 202.3 | 2.599 | 49-55C
52 | 0.4 | 525.8 | 194.7 | 2.699 | 49-55C
51 | 0.4 | 525.8 | 187.4 | 2.807 | 49-55C
50 | 0.4 | 525.8 | 180.7 | 2.909 | 49-55C
49 | 0.4 | 525.8 | 174.4 | 3.016 | 49-55C

## Low_Ambient_Notes
ACC_2 Solver_Curve Low-Ambient Extension
Purpose | Supplement the active Solver_Curve with engineering-estimated low ambient points from -10°C to 35°C.
Data status | Low-ambient rows are engineering estimates only, not vendor-certified performance data.
Active Solver_Curve | Uses load_ratio 0.5 to 1.0 across -10°C to 55°C for a consistent lookup grid.
Original data | The original uploaded Solver_Curve is preserved in Solver_Curve_Original.
0.4 load_ratio note | Original 49–55°C vendor rows at load_ratio 0.4 are preserved in Solver_Curve_Original but excluded from active Solver_Curve to avoid an inconsistent grid.
Source labels | estimated_low_ambient = engineering estimate; 38-48C and 49-55C = original uploaded workbook data.
Use in reports | State that ACC performance below 38°C is estimated and should be replaced with vendor data when available.